{"text_format":"1","workbook":"xlsx","n_sheets":18,"sheets":["Instructions","Criteria","Menu","Cl2 Input Data","Cl2 Dose Summary","Cl2 Residual Summary","Cl2 Dose and Residual Summary","Cl2 Demand Summary","DataEntryPaste(CT)","DataEntryValues(CT)","Disinfection Summary","Total Inact Ratio","Segment Inact Ratio","pH Summary","ChloramineCT","ClO2-CT","AllDataSort","MonthDist"],"not_rendered":{"charts":10,"images":1,"macros":1,"external_links":0,"defined_names":117,"comments":3,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Instructions","index":0,"n_rows":64,"n_cols":4,"rows_kept":64,"cut":false,"hidden":true,"merged":[]}
["Historical Cl2 and CT Spreadsheet"]
[null,"Instructions"]
["> The purpose of this database is to assess a water system's historical chlorine dose and residual and"]
["disinfection (CT) performance data."]
["> The Cl2 input data requires chlorine dose and plant residual data."]
["> The CT database requires data needed to develop the CT profile, including plant flow rate, pH, temperature"]
["residuals, volume and baffling factors for various segments through the plant. "]
["> The State-specific CT requirement should be entered into the appropriate cell on the DataEntryValues(CT)"]
["worksheet.  If the State has a more stringent CT goal for their systems, this should be entered as well; "]
["otherwise, a CT goal of twice the required amount will be calculated.  The goal will be shown on the CT plots."]
["> The residual data needed to develop the CT profile is also needed used for the chlorine residual analysis; "]
["while it must be entered on two different worksheets, it can be copied/pasted to minimize data entry."]
[]
[]
[]
["The following is helpful for entering the CT data."]
["Entering data from another spreadsheet (copy/paste):"]
["1.","When entering (copying) data sets from another spreadsheet, use the DataEntryPaste worksheet.  This"]
[null,"will reduce problems that could occur due to formatting differences.  Typically, this worksheet is only"]
[null,"used to start a plant disinfection profile.  To enter new data at a later time, use the DataEntryValues"]
[null,"worksheet."]
["2.","Before entering new data, you should clear the data entry area of any pre-existing data.  This can be"]
[null,"performed by clicking on the CLEAR button."]
["3.","After the data is entered, click the TRANSFER button to transfer the data to the database."]
[null,"A message will appear notifying the user that the data in the database (DataEntryValues worksheet)"]
[null,"will be replaced."]
["4.","Go to the DataEntryValues worksheet and enter the plant name, inactivation target, and segment"]
[null,"information (i.e., volume, baffle factor)."]
["5.","Click the UPDATE button to develop the summary report."]
[]
["Entering individual data from plant records:"]
["1.","When entering data from plant records, use the DataEntryValues worksheet."]
["2.","Before entering new data, you should clear the database of any pre-existing data.  This can be "]
[null,"performed by clicking on the CLEAR button."]
["3.","Enter the plant name, inactivation target, and segment information (i.e., volume, baffle factor)."]
["4.","After data is entered, click on the UPDATE button to develop the Summary Report."]
[]
[]
[]
[]
[]
[]
[null,null,{"$f":"A1","v":"Historical Cl2 and CT Spreadsheet"}]
[null,null,"FILE:","Cl2&CTspreadsheetV1.xls"]
[null,null,"AUTHOR:","L. DeMers"]
[null,null,"COMPANY:","Process Applications, Inc."]
[null,null,"PURPOSE:","To assess inactivation ratio for a water treatment plant"]
[]
[null,"DATE MODIFIED:",null,"MODIFICATIONS & BY WHOM:"]
[null,"2000-04-29","LDD modified Optimization Assessment Software (turbidity) to calculate inactivation"]
[null,null,"ratio (CT measured/CT required)."]
[null,"2001-08-30","LDD modified data entry to accommodate leap year."]
[null,"2002-02-23","LDD added annual statistics for chlorine residual, pH, and temperature for each"]
[null,null,"segment.  Also added comments to make spreadsheet more user friendly."]
[null,"2002-07-01","LDD modified section 5 to allow input of varying water level in a basin such as a"]
[null,null,"clearwell."]
[null,"2002-10-09","LDD corrected error in segment 5 in MonthDist worksheet.  Formula did not include basin"]
[null,null,"depth in calculation."]
[null,"2004-09-23","LDD combined historical chlorine dose and residual spreadsheet with CT spreadsheet."]
[null,"2006-03-21","Update spreadsheet for DBP PBT.  Removed DS chlorine residual data to make"]
[null,null,"spreadsheet plant-based information only.  Modified charts to show disinfection ratio"]
[null,null,"for each segment and total."]
[]
[null,"Model by: Process Applications, Inc. Fort Collins, CO 970-223-5787"]

{"sheet":"Criteria","index":1,"n_rows":7,"n_cols":11,"rows_kept":7,"cut":false,"hidden":true,"merged":[]}
[null,"MenuSheetLink",1,null,null,"MenuSheetLink1",1,null,null,"MenuSheetLink2",1]
[null,null,"Select Data Entry",null,null,null,"Select Chlorine Charts",null,null,null,"Select CT Charts"]
[null,null,"Menu",null,null,null,"Menu",null,null,null,"Menu"]
[null,null,"Chlorine Dose & Residual",null,null,null,"Chlorine Dose",null,null,null,"Disinfection Summary"]
[null,null,"CT Input Data (paste values)",null,null,null,"Chlorine Residual",null,null,null,"Total Inactivation Ratio"]
[null,null,"CT Input Data (enter values)",null,null,null,"Chlorine Dose & Residual",null,null,null,"Segment Inactivation Ratio"]
[null,null,null,null,null,null,"Chlorine Demand",null,null,null,"pH Summary"]

{"sheet":"Menu","index":2,"n_rows":21,"n_cols":3,"rows_kept":21,"cut":false,"hidden":false,"merged":[]}
[]
[]
[]
[]
[null,"Plant/System Name","Watertown Waterworks"]
[null,"Plant PWS #","ABC123456"]
[]
[]
[]
[null,"This spreadsheet is used to trend chlorine dose and residal data within a treatment plant for 1 year:"]
[null,"Chlorine dose at two locations (e.g., pre and post)"]
[null,"Chlorine residual at two locations (e.g., settled, finished)"]
[]
[]
[]
[null,"This speadsheet is also used to develop a disinfection profile for a plant for 1 year:"]
[null,"Include up to five disinfection segments"]
[null,"Input maximum daily plant flow rate (one location)"]
[null,"Input minimum daily chlorine residual for each segment"]
[null,"Input minimum daily temperature for each segment"]
[null,"Input maximum daily pH for each segment"]

{"sheet":"Cl2 Input Data","index":3,"n_rows":374,"n_cols":19,"rows_kept":374,"cut":false,"hidden":true,"merged":[[6,1,7,1],[6,2,7,2],[6,3,7,3],[6,18,7,18],[6,17,7,17],[6,4,7,4],[6,13,7,13]]}
[]
["Minimum",{"$f":"MIN(B9:B374)","v":0},0,0,0,0,0,0,0,0,0,{"$f":"MIN(L9:L374)","v":0},{"$f":"MIN(F9:K374)","v":0},null,null,null,null,{"$f":"MIN(R9:R374)","v":0},{"$f":"MIN(S9:S374)","v":0}]
["Maximum",{"$f":"MAX(B9:B374)","v":0},0,0,0,0,0,0,0,0,0,{"$f":"MAX(L9:L374)","v":0},{"$f":"MAX(F9:K374)","v":0},null,null,null,null,{"$f":"MAX(R9:R374)","v":0},{"$f":"MAX(S9:S374)","v":0}]
["Average",{"$f":"IF(SUM(B9:B374)=0,,AVERAGE(B9:B374))","v":0},{"$f":"IF(SUM(C9:C374)=0,,AVERAGE(C9:C374))","v":0},0,0,0,0,0,0,0,0,{"$f":"IF(SUM(L9:L374)=0,,AVERAGE(L9:L374))","v":0},{"$f":"IF(SUM(F9:K374)=0,,AVERAGE(F9:K374))","v":0},null,null,null,null,{"$f":"IF(SUM(R9:R374)=0,,AVERAGE(R9:R374))","v":0},{"$f":"IF(SUM(S9:S374)=0,,AVERAGE(S9:S374))","v":0}]
[]
[]
["Dose & Res.","Pre Cl2 Dose","Post Cl2 Dose","Total Cl2 Dose","Settled Residual","Plant Finished Residual",null,null,null,null,null,null,null,"Plant Finished Res. Target",null,null,null,"Pre Chlorine Demand (mg/L)","Total Demand (Total Dose - PE Residual)"]
["as mg/L >>",null,null,null,null,"04:00:00","08:00:00","12:00:00","16:00:00","20:00:00",1,"Daily Avg.","Daily Min."]
["2017-01-01",null,null,{"$f":"B9+C9","v":0},null,null,null,null,null,null,null,{"$f":"IF(SUM(F9:K9)=0,,AVERAGE(F9:K9))","v":0},{"$f":"MIN(F9:K9)","v":0},0.9,null,null,null,{"$f":"IF(B9-E9>0,B9-E9,\"\")","v":""},{"$f":"IF(D9-M9>0,D9-M9,\"\")","v":""}]
[{"$f":"+A9+1","v":"2017-01-02"},null,null,{"$f":"B10+C10","v":0},null,null,null,null,null,null,null,{"$f":"IF(SUM(F10:K10)=0,,AVERAGE(F10:K10))","v":0},{"$f":"MIN(F10:K10)","v":0},{"$f":"N9","v":0.9},null,null,null,{"$f":"IF(B10-E10>0,B10-E10,\"\")","v":""},""]
[{"$f":"+A10+1","v":"2017-01-03"},null,null,0,null,null,null,null,null,null,null,0,0,{"$f":"N10","v":0.9},null,null,null,"",""]
["2017-01-04",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-01-05",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-01-06",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-01-07",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-01-08",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-01-09",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-01-10",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-01-11",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-01-12",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-01-13",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-01-14",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-01-15",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-01-16",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-01-17",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-01-18",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-01-19",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-01-20",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-01-21",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-01-22",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-01-23",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-01-24",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-01-25",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-01-26",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-01-27",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-01-28",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-01-29",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-01-30",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-01-31",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-02-01",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-02-02",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-02-03",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-02-04",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-02-05",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-02-06",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-02-07",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-02-08",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-02-09",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-02-10",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-02-11",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-02-12",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-02-13",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-02-14",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-02-15",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-02-16",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-02-17",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-02-18",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-02-19",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-02-20",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-02-21",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-02-22",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-02-23",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-02-24",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-02-25",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-02-26",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-02-27",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-02-28",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-03-01",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-03-02",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-03-03",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-03-04",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-03-05",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-03-06",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",{"$f":"IF(D73-M73>0,D73-M73,\"\")","v":""}]
["2017-03-07",null,null,{"$f":"B74+C74","v":0},null,null,null,null,null,null,null,{"$f":"IF(SUM(F74:K74)=0,,AVERAGE(F74:K74))","v":0},{"$f":"MIN(F74:K74)","v":0},0.9,null,null,null,{"$f":"IF(B74-E74>0,B74-E74,\"\")","v":""},""]
[{"$f":"+A74+1","v":"2017-03-08"},null,null,0,null,null,null,null,null,null,null,0,0,{"$f":"N74","v":0.9},null,null,null,"",""]
["2017-03-09",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-03-10",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-03-11",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-03-12",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-03-13",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-03-14",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-03-15",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-03-16",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-03-17",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-03-18",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-03-19",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-03-20",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-03-21",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-03-22",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-03-23",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-03-24",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-03-25",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-03-26",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-03-27",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-03-28",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-03-29",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-03-30",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-03-31",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-01",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-02",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-03",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-04",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-05",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-06",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-07",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-08",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-09",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-10",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-11",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-12",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-13",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-14",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-15",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-16",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-17",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-18",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-19",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-20",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-21",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-22",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-23",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-24",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-25",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-26",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-27",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-28",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-29",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-04-30",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-05-01",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-05-02",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-05-03",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-05-04",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-05-05",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-05-06",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-05-07",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-05-08",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-05-09",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",{"$f":"IF(D137-M137>0,D137-M137,\"\")","v":""}]
["2017-05-10",null,null,{"$f":"B138+C138","v":0},null,null,null,null,null,null,null,{"$f":"IF(SUM(F138:K138)=0,,AVERAGE(F138:K138))","v":0},{"$f":"MIN(F138:K138)","v":0},0.9,null,null,null,{"$f":"IF(B138-E138>0,B138-E138,\"\")","v":""},""]
[{"$f":"+A138+1","v":"2017-05-11"},null,null,0,null,null,null,null,null,null,null,0,0,{"$f":"N138","v":0.9},null,null,null,"",""]
["2017-05-12",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-05-13",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-05-14",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-05-15",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-05-16",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-05-17",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-05-18",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-05-19",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-05-20",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-05-21",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-05-22",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-05-23",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-05-24",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-05-25",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-05-26",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-05-27",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-05-28",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-05-29",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-05-30",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-05-31",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-01",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-02",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-03",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-04",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-05",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-06",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-07",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-08",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-09",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-10",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-11",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-12",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-13",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-14",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-15",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-16",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-17",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-18",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-19",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-20",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-21",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-22",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-23",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-24",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-25",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-26",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-27",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-28",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-29",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-06-30",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-07-01",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-07-02",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-07-03",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-07-04",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-07-05",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-07-06",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-07-07",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-07-08",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-07-09",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-07-10",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-07-11",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-07-12",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",{"$f":"IF(D201-M201>0,D201-M201,\"\")","v":""}]
["2017-07-13",null,null,{"$f":"B202+C202","v":0},null,null,null,null,null,null,null,{"$f":"IF(SUM(F202:K202)=0,,AVERAGE(F202:K202))","v":0},{"$f":"MIN(F202:K202)","v":0},0.9,null,null,null,{"$f":"IF(B202-E202>0,B202-E202,\"\")","v":""},""]
[{"$f":"+A202+1","v":"2017-07-14"},null,null,0,null,null,null,null,null,null,null,0,0,{"$f":"N202","v":0.9},null,null,null,"",""]
["2017-07-15",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-07-16",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-07-17",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-07-18",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-07-19",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-07-20",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-07-21",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-07-22",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-07-23",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-07-24",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-07-25",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-07-26",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-07-27",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-07-28",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-07-29",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-07-30",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-07-31",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-01",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-02",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-03",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-04",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-05",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-06",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-07",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-08",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-09",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-10",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-11",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-12",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-13",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-14",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-15",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-16",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-17",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-18",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-19",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-20",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-21",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-22",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-23",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-24",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-25",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-26",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-27",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-28",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-29",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-30",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-08-31",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-09-01",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-09-02",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-09-03",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-09-04",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-09-05",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-09-06",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-09-07",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-09-08",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-09-09",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-09-10",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-09-11",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-09-12",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-09-13",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-09-14",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",{"$f":"IF(D265-M265>0,D265-M265,\"\")","v":""}]
["2017-09-15",null,null,{"$f":"B266+C266","v":0},null,null,null,null,null,null,null,{"$f":"IF(SUM(F266:K266)=0,,AVERAGE(F266:K266))","v":0},{"$f":"MIN(F266:K266)","v":0},0.9,null,null,null,{"$f":"IF(B266-E266>0,B266-E266,\"\")","v":""},""]
[{"$f":"+A266+1","v":"2017-09-16"},null,null,0,null,null,null,null,null,null,null,0,0,{"$f":"N266","v":0.9},null,null,null,"",""]
["2017-09-17",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-09-18",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-09-19",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-09-20",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-09-21",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-09-22",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-09-23",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-09-24",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-09-25",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-09-26",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-09-27",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-09-28",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-09-29",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-09-30",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-01",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-02",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-03",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-04",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-05",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-06",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-07",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-08",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-09",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-10",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-11",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-12",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-13",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-14",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-15",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-16",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-17",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-18",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-19",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-20",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-21",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-22",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-23",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-24",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-25",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-26",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-27",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-28",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-29",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-30",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-10-31",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-11-01",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-11-02",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-11-03",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-11-04",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-11-05",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-11-06",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-11-07",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-11-08",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-11-09",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-11-10",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-11-11",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-11-12",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-11-13",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-11-14",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-11-15",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-11-16",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-11-17",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",{"$f":"IF(D329-M329>0,D329-M329,\"\")","v":""}]
["2017-11-18",null,null,{"$f":"B330+C330","v":0},null,null,null,null,null,null,null,{"$f":"IF(SUM(F330:K330)=0,,AVERAGE(F330:K330))","v":0},{"$f":"MIN(F330:K330)","v":0},0.9,null,null,null,{"$f":"IF(B330-E330>0,B330-E330,\"\")","v":""},""]
[{"$f":"+A330+1","v":"2017-11-19"},null,null,0,null,null,null,null,null,null,null,0,0,{"$f":"N330","v":0.9},null,null,null,"",""]
["2017-11-20",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-11-21",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-11-22",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-11-23",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-11-24",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-11-25",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-11-26",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-11-27",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-11-28",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-11-29",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-11-30",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-12-01",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-12-02",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-12-03",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-12-04",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-12-05",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-12-06",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-12-07",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-12-08",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-12-09",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-12-10",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-12-11",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-12-12",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-12-13",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-12-14",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-12-15",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-12-16",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-12-17",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-12-18",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-12-19",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-12-20",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-12-21",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-12-22",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-12-23",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-12-24",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-12-25",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-12-26",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-12-27",null,null,0,null,null,null,null,null,null,null,0,0,0.9,null,null,null,"",""]
["2017-12-28",null,null,{"$f":"B370+C370","v":0},null,null,null,null,null,null,null,0,{"$f":"MIN(F370:K370)","v":0},0.9,null,null,null,"",""]
["2017-12-29",null,null,{"$f":"B371+C371","v":0},null,null,null,null,null,null,null,0,{"$f":"MIN(F371:K371)","v":0},0.9,null,null,null,"",""]
["2017-12-30",null,null,{"$f":"B372+C372","v":0},null,null,null,null,null,null,null,0,{"$f":"MIN(F372:K372)","v":0},0.9,null,null,null,"",""]
["2017-12-31",null,null,{"$f":"B373+C373","v":0},null,null,null,null,null,null,null,0,{"$f":"MIN(F373:K373)","v":0},0.9,null,null,null,"",""]
["2018-01-01",null,null,null,null,null,null,null,null,null,null,0,{"$f":"MIN(F374:K374)","v":0},0.9,null,null,null,"",""]

{"sheet":"Cl2 Dose Summary","index":4,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":true,"merged":[]}

{"sheet":"Cl2 Residual Summary","index":5,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":true,"merged":[]}

{"sheet":"Cl2 Dose and Residual Summary","index":6,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":true,"merged":[]}

{"sheet":"Cl2 Demand Summary","index":7,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":true,"merged":[]}

{"sheet":"DataEntryPaste(CT)","index":8,"n_rows":384,"n_cols":18,"rows_kept":384,"cut":false,"hidden":true,"merged":[[14,2,14,4],[14,5,14,7],[14,8,14,10],[14,11,14,13]]}
[]
[]
[]
[null,"Instruction to users:  Paste plant data into the data entry area below.  The "]
[null,"data entry area will hold 366 days of data.  Following data input, transfer data to the"]
[null,"database by clicking on the data TRANSFER button.  Go to the DataEntryValues "]
[null,"worksheet to enter the plant name and performance goals."]
[]
[]
[null,null,null,null,null,null,null,null,null,null,"Using this button will transfer data from this worksheet to the DataEntryValues"]
[null,null,null,null,null,null,null,null,null,null,"worksheet.  All existing data in the DataEntryValues will be overwritten."]
[]
[]
["Data Entry Area for Posting Data Sets"]
[null,null,{"$f":"CONCATENATE(\"Segment 1 - \",'DataEntryValues(CT)'!$F$6)","v":"Segment 1 - "},null,null,{"$f":"CONCATENATE(\"Segment 2 - \",'DataEntryValues(CT)'!$F$9)","v":"Segment 2 - "},null,null,{"$f":"CONCATENATE(\"Segment 3 - \",'DataEntryValues(CT)'!$F$12)","v":"Segment 3 - "},null,null,{"$f":"CONCATENATE(\"Segment 4 - \",'DataEntryValues(CT)'!$F$15)","v":"Segment 4 - "},null,null,{"$f":"CONCATENATE(\"Segment 5 - \",$F$17)","v":"Segment 5 - mg/L"}]
["Date","Flow","Residual","pH","Temp.","Residual","pH","Temp.","Residual","pH","Temp.","Residual","pH","Temp.","Depth","Residual","pH","Temp."]
[null,"gpm","mg/L",null,"C","mg/L",null,"C","mg/L",null,"C","mg/L",null,"C","ft","mg/L",null,"C"]
["2017-01-01",4128.4861111111113,1.1499999999999999,7.13,5.5,0.64,7.06,5.2,null,null,null,null,null,null,13.7,0.71,7.2,4.9000000000000004]
[{"$f":"A18+1","v":"2017-01-02"},3944.661111111111,1.59,7.05,6.1,0.7,7.11,6.2,null,null,null,null,null,null,13.6,0.87,7.3,5.2]
[{"$f":"A19+1","v":"2017-01-03"},3980.7180555555556,1.34,6.95,5.2,0.76,7.06,5.3,null,null,null,null,null,null,13.3,0.75,7.2,5.6]
["2017-01-04",3847.9569444444446,1.64,7.09,5.6,0.88,7.1,5.6,null,null,null,null,null,null,11.4,0.8,7.1,5.8]
["2017-01-05",4073.4756944444443,1.6,6.9,5.5,0.5,6.8,5.5,null,null,null,null,null,null,13.7,0.8,7.1,5.5]
["2017-01-06",3936.1291666666666,1.4,7.17,6.2,0.77,7.09,6,null,null,null,null,null,null,14.5,0.7,7.2,4.7]
["2017-01-07",3894.0187500000002,1.6,7.07,5.4,0.77,7.09,5.6,null,null,null,null,null,null,13.4,0.8,7.1,4.5999999999999996]
["2017-01-08",4003.7840277777777,1.01,7.09,4.8,0.85,7.09,5.6,null,null,null,null,null,null,14.2,0.7,7.1,4.8]
["2017-01-09",4317.3166666666666,1.17,7.09,5,1.03,7.08,5,null,null,null,null,null,null,13,0.7,7.2,4.7]
["2017-01-10",3821.2680555555557,1.47,7.17,4.8,0.36,7.16,4.9000000000000004,null,null,null,null,null,null,12.9,0.7,7.2,4.9000000000000004]
["2017-01-11",4111.1034722222221,1.18,7.04,5.0999999999999996,0.82,7.1,5.9,null,null,null,null,null,null,13.3,0.8,7.2,4.8]
["2017-01-12",4337.7791666666662,1.5,7.16,5.0999999999999996,0.9,7.16,4.7,null,null,null,null,null,null,13.5,0.78,7.2,4.7]
["2017-01-13",4042.0034722222222,1.5,7.16,5,0.75,7.11,4.8,null,null,null,null,null,null,13,0.89,7.2,4.7]
["2017-01-14",3733.1326388888888,1.6,7.14,5.0999999999999996,0.83,7.15,4.7,null,null,null,null,null,null,13,0.7,7.3,4.9000000000000004]
["2017-01-15",3739.2430555555557,0.94,6.93,5.0999999999999996,0.82,7.05,4.7,null,null,null,null,null,null,12,0.7,7.1,5]
["2017-01-16",3603.4812499999998,1.31,7.08,5.5,1.26,7.04,5.3,null,null,null,null,null,null,13.5,0.85,7.1,5.2]
["2017-01-17",3260.036111111111,1.38,7.05,4.9000000000000004,0.88,7.07,5,null,null,null,null,null,null,11.8,0.79,7.1,4.5]
["2017-01-18",3466.5430555555554,1.34,7.14,5.0999999999999996,0.93,7.1,5.0999999999999996,null,null,null,null,null,null,13,0.89,7.2,4.9000000000000004]
["2017-01-19",3810.4916666666668,1.29,7.09,5.0999999999999996,0.99,7.1,5.0999999999999996,null,null,null,null,null,null,12.5,0.84,7.2,5.2]
["2017-01-20",3611.1305555555555,1.1000000000000001,7.08,6.9,0.98,7,5.4,null,null,null,null,null,null,14.2,0.8,7.1,4.4000000000000004]
["2017-01-21",3617.3048611111112,1.6,7.06,5.3,0.53,7.09,5.5,null,null,null,null,null,null,12.9,0.9,7.1,5.2]
["2017-01-22",3808.3826388888888,1.45,7.1,5.9,1.04,7.11,5.8,null,null,null,null,null,null,11.9,0.87,7.1,5.2]
["2017-01-23",3783.9513888888887,1.43,7.06,6,0.98,7.07,5.9,null,null,null,null,null,null,11.9,0.9,7.2,5.5]
["2017-01-24",3483.5652777777777,1.24,7.17,5.7,0.9,7.16,5.4,null,null,null,null,null,null,12.5,0.9,7.2,5.4]
["2017-01-25",3413.7541666666666,1.24,7.18,5.2,0.96,7.23,5.3,null,null,null,null,null,null,12.5,0.9,7.2,5.0999999999999996]
["2017-01-26",3520.3979166666668,1.05,7.25,5.5,0.87,7.09,5.3,null,null,null,null,null,null,13.2,0.9,7.1,5.3]
["2017-01-27",3542.2506944444444,1.1599999999999999,7.16,6.1,0.79,7.04,6.2,null,null,null,null,null,null,13.6,0.87,7.3,6]
["2017-01-28",3506.2361111111113,1.17,7.05,6,0.9,7.02,6.1,null,null,null,null,null,null,14.2,0.9,7.2,6.4]
["2017-01-29",3442.1125000000002,0.95,6.92,5.9,0.9,7,6,null,null,null,null,null,null,12.8,0.8,7.1,6]
["2017-01-30",3596.7291666666665,1.08,7.13,6.4,0.85,7.13,6.4,null,null,null,null,null,null,13.2,0.86,7.2,6.1]
["2017-01-31",3623.0895833333334,1.18,7.17,5.9,0.7,7.01,5.7,null,null,null,null,null,null,12.4,0.9,7.2,6.1]
["2017-02-01",3619.4219061458152,1.62,7.26,5.8,1.2,7,6,null,null,null,null,null,null,11.3,1.7,7.1,5.4]
["2017-02-02",4143.1265691404933,1.88,7.13,5.7,1.52,7.15,5.7,null,null,null,null,null,null,14.3,1.67,7.2,5.8]
["2017-02-03",4134.0956158355057,1.8,7.06,6.4,1.19,7.08,5.9,null,null,null,null,null,null,13.6,1.82,7.1,6.8]
["2017-02-04",3394.5612755668039,1.63,7.1,5.7,1.49,7.05,5.5,null,null,null,null,null,null,13.9,1.65,7.2,6.3]
["2017-02-05",3814.2793284125141,1.72,7.07,6.8,1.24,7.09,7,null,null,null,null,null,null,13.6,1.1000000000000001,7.3,6.3]
["2017-02-06",3449.3895330821088,1.4,7.12,6.4,1,7.12,6.8,null,null,null,null,null,null,13.9,1,7.1,6.9]
["2017-02-07",3326.7904066213964,1.32,7.13,6.8,1.21,7.15,7.6,null,null,null,null,null,null,13.9,1.02,7.2,7.6]
["2017-02-08",4267.0623297568318,1.1200000000000001,7.11,10.7,0.96,6.94,8.3000000000000007,null,null,null,null,null,null,13.9,0.8,7.2,8.5]
["2017-02-09",4255.4973694014761,1.43,7.08,8.8000000000000007,1.1100000000000001,7.08,8.4,null,null,null,null,null,null,13,1,7.2,8.4]
["2017-02-10",3327.1671088692751,1.19,7.15,8,0.8,7.04,8.1999999999999993,null,null,null,null,null,null,14.4,1.2,7.2,8.3000000000000007]
["2017-02-11",3707.0647886117667,1.2,7.18,8.1999999999999993,0.8,7.08,8.1,null,null,null,null,null,null,14.5,1.2,7.2,8.1999999999999993]
["2017-02-12",4253.9192240697257,1.32,7.12,9.1999999999999993,0.96,7.1,8.9,null,null,null,null,null,null,15.1,1.2,7.2,8.8000000000000007]
["2017-02-13",4244.2446457170354,1.32,7.14,9.8000000000000007,0.92,7.06,9.1,null,null,null,null,null,null,14.3,1.04,7.1,9.1]
["2017-02-14",3822.9018003953297,1.22,7.12,9.1,0.76,7.1,9.1999999999999993,null,null,null,null,null,null,14.7,1.1100000000000001,7.2,9.9]
["2017-02-15",3959.599097909645,1.28,6.89,10.3,0.87,6.98,9.6,null,null,null,null,null,null,13.6,1.22,7.1,10.7]
["2017-02-16",3268.0281124761354,1.42,7.11,9.8000000000000007,0.8,7.13,9.9,null,null,null,null,null,null,11.7,1.23,7.2,9.3000000000000007]
["2017-02-17",3316.779720414424,1.2,7.06,10.1,0.92,7.09,10,null,null,null,null,null,null,13.4,1.3,7.1,9]
["2017-02-18",4130.3934066148222,1.3,7.02,10.6,0.8,7.04,10.3,null,null,null,null,null,null,13.7,1.3,7.1,9.9]
["2017-02-19",3963.5634820578025,1.31,7.07,10.1,0.88,7.06,10.3,null,null,null,null,null,null,10.1,0.8,7.2,8.9]
["2017-02-20",3436.3377628929306,1.22,7.12,10.6,0.98,7.14,10.6,null,null,null,null,null,null,10.6,0.87,7.1,10.4]
["2017-02-21",3622.2508119190088,0.82,7.14,10.8,0.81,7.18,10.7,null,null,null,null,null,null,13.7,0.8,7.2,10.4]
["2017-02-22",3680.365047293868,1.39,7.14,11.9,1.05,7.07,11.1,null,null,null,null,null,null,12.4,0.6,7.1,10.8]
["2017-02-23",4337.6958814041564,1.55,7.25,12.5,0.84,7.27,12.3,null,null,null,null,null,null,13,0.87,7.2,11.3]
["2017-02-24",3283.6577769867663,1.2,7.12,10.8,0.94,7.05,10.9,null,null,null,null,null,null,11.6,0.97,7.1,11.4]
["2017-02-25",4026.2637111137865,1.1200000000000001,7.05,10.1,0.99,7.08,9.9,null,null,null,null,null,null,9.6,0.8,7.1,11.2]
["2017-02-26",4006.009802698979,0.75,7.04,11.8,0.55000000000000004,6.68,10.8,null,null,null,null,null,null,10,0.69,7.1,11.3]
["2017-02-27",3594.7053042190209,1,7.13,11,0.73,7.14,10.9,null,null,null,null,null,null,14,0.9,7.1,10.9]
["2017-02-28",4318.4408445550207,1.03,7.13,11.7,0.6,7.13,11.2,null,null,null,null,null,null,13.9,0.92,7.2,11]
["2017-03-01",3627.9005199200537,1.08,7.06,12.1,0.79,7.05,12.1,null,null,null,null,null,null,14.5,1,7.1,11.9]
["2017-03-02",3855.302170838389,1.28,7.08,13,0.79,7.08,12.9,null,null,null,null,null,null,13.3,0.86,7.1,12.4]
["2017-03-03",4010.8984539197681,1.7,7.05,11.9,0.7,7.05,12,null,null,null,null,null,null,14.1,1,7.1,12.1]
["2017-03-04",3430.9530761545479,1.3,7.14,12.3,0.6,7.05,13.7,null,null,null,null,null,null,14.5,0.96,7.1,13.6]
["2017-03-05",3814.5050022914447,0.92,7.05,14.7,0.48,7.07,14.8,null,null,null,null,null,null,10.9,0.97,7.2,14]
["2017-03-06",3733.0325583170679,1.4,6.9,14.7,0.7,6.99,14.5,null,null,null,null,null,null,10.8,1.02,7.1,14]
["2017-03-07",3941.9624771079102,0.64,7.13,13.7,0.87,7,13.7,null,null,null,null,null,null,11.2,0.89,7.2,12.6]
[{"$f":"A83+1","v":"2017-03-08"},4007.2024283483715,1.2,7.09,14.2,0.61,7.1,13.8,null,null,null,null,null,null,13.9,0.96,7.1,15.3]
["2017-03-09",3434.301049584903,0.84,7.1,14.3,0.47,7.03,14.5,null,null,null,null,null,null,13.7,0.92,7.1,14.2]
["2017-03-10",3617.790271779319,1.1000000000000001,7.1,15.4,0.38,7.08,15.2,null,null,null,null,null,null,12.3,0.97,7.1,14]
["2017-03-11",4297.9292582036078,1.2,7.06,15,0.52,7.12,15,null,null,null,null,null,null,13,1,7.1,14.4]
["2017-03-12",4198.6434228694779,1.2,7.08,15.1,0.78,7.09,15.1,null,null,null,null,null,null,11.9,0.99,7.1,14.5]
["2017-03-13",3880.0382568136033,1.06,6.92,14.5,0.54,6.97,14.7,null,null,null,null,null,null,9.1999999999999993,1.05,7.1,14.5]
["2017-03-14",4224.0780118126368,1.03,7.13,14.9,0.65,7.08,14.6,null,null,null,null,null,null,9,0.92,7.1,14.6]
["2017-03-15",4171.0957460450054,0.88,6.97,15.8,0.47,6.99,15.7,null,null,null,null,null,null,12.6,0.98,7,14.6]
["2017-03-16",3751.4245153879665,1.04,6.98,15.1,0.4,7.02,15.1,null,null,null,null,null,null,9.9,0.99,7.1,14.6]
["2017-03-17",3744.619932440618,0.93,7.04,15.5,0.52,7.08,15.6,null,null,null,null,null,null,11.9,0.91,7.2,15.4]
["2017-03-18",3934.0853668979221,0.7,7.1,15.2,0.49,7.14,15.2,null,null,null,null,null,null,11.5,0.9,7.2,15.8]
["2017-03-19",3275.3192656299443,0.7,7.04,15.2,0.39,7.04,16.3,null,null,null,null,null,null,11.6,0.91,7.1,15.6]
["2017-03-20",3968.5993186723895,0.57999999999999996,7.13,15.8,0.31,7.2,15.9,null,null,null,null,null,null,11.6,0.89,7.2,16.100000000000001]
["2017-03-21",4276.6276573688037,0.57999999999999996,7.27,16.3,0.37,7.19,15.8,null,null,null,null,null,null,10.3,0.93,7.1,16.3]
["2017-03-22",4226.1080215770162,0.48,7.12,15.7,0.3,7.1,16,null,null,null,null,null,null,12.9,0.97,7.1,16.100000000000001]
["2017-03-23",3975.1776039035776,0.76,7.18,16.5,0.36,7.22,16.3,null,null,null,null,null,null,11.9,0.95,7.3,16]
["2017-03-24",3461.7811397390556,0.72,7.12,16.899999999999999,0.3,7.09,16.899999999999999,null,null,null,null,null,null,13.9,1.1000000000000001,7.1,16]
["2017-03-25",4202.5618195960596,0.86,7.11,16.899999999999999,0.3,7.1,17,null,null,null,null,null,null,14.4,1.05,7.1,15]
["2017-03-26",3718.2337130244318,0.85,7.02,16.7,0.45,7.11,16.8,null,null,null,null,null,null,13.4,0.82,7.1,16.600000000000001]
["2017-03-27",4021.0561675138242,0.26,6.97,16.7,0.09,6.98,16.899999999999999,null,null,null,null,null,null,13.6,0.94,7.1,17]
["2017-03-28",3459.9809739554457,1.02,7.05,16.600000000000001,0.3,7.14,16.7,null,null,null,null,null,null,9.6999999999999993,1.02,7.1,16.8]
["2017-03-29",3939.8436228299593,0.85,7.02,17.2,0.31,7.09,17,null,null,null,null,null,null,10.5,0.98,7.1,16.7]
["2017-03-30",3428.9516841378172,1.35,7.04,16.899999999999999,0.76,7.06,16.899999999999999,null,null,null,null,null,null,10.6,1.01,7.1,16.100000000000001]
["2017-03-31",3354.9187936610051,1.1000000000000001,7.09,17.2,0.39,7.09,17,null,null,null,null,null,null,10.8,1.03,7.1,16.600000000000001]
["2017-04-01",4311.6499695049406,1.2,7.05,16.7,0.39,7.11,16.8,null,null,null,null,null,null,13.3,0.9,7.1,15.6]
["2017-04-02",4224.1912849769215,1.1599999999999999,7.05,17.3,0.69,6.97,17.100000000000001,null,null,null,null,null,null,12.5,0.92,7.1,17]
["2017-04-03",3877.2594952382742,0.86,7.17,17.2,0.56999999999999995,7.18,17.3,null,null,null,null,null,null,11.6,0.88,7.2,16.7]
["2017-04-04",3914.1983468185817,0.98,7.13,16.3,0.53,7.05,16.600000000000001,null,null,null,null,null,null,11,0.87,7.1,17]
["2017-04-05",4295.8149567967594,1.06,7.03,17.3,0.77,7.05,17.399999999999999,null,null,null,null,null,null,11,1,7.1,17]
["2017-04-06",3531.7498208625134,0.84,7.2,17,0.56999999999999995,7.09,17.100000000000001,null,null,null,null,null,null,13.7,1,7.1,16.7]
["2017-04-07",4141.6633328561966,0.65,7.05,16.5,0.38,7.01,16.7,null,null,null,null,null,null,11.9,0.97,7.1,16.8]
["2017-04-08",3358.3588716395993,0.82,7.07,16.399999999999999,0.56999999999999995,7.03,16.399999999999999,null,null,null,null,null,null,10,0.89,7.1,17.2]
["2017-04-09",3794.8615297681245,0.89,7.06,16.600000000000001,0.47,7.01,16.600000000000001,null,null,null,null,null,null,11.3,1,7.1,16.899999999999999]
["2017-04-10",3621.0576656084127,0.9,7.02,17,0.52,7.08,17.2,null,null,null,null,null,null,14.2,0.88,7.1,16.600000000000001]
["2017-04-11",3829.7808882308996,0.59,7.17,17.399999999999999,0.12,7.08,17.5,null,null,null,null,null,null,11.3,1,7.1,17.3]
["2017-04-12",3900.8391691921966,1.1399999999999999,7.05,17.7,0.43,7,17.5,null,null,null,null,null,null,14.8,1,7.1,17.3]
["2017-04-13",4266.9555177079128,0.65,6.95,18.3,0.32,7.1,18,null,null,null,null,null,null,12.2,0.71,7.1,18.100000000000001]
["2017-04-14",3998.1985756050453,0.83,7.11,17.2,0.3,7.05,17,null,null,null,null,null,null,13.2,0.8,7.1,17.600000000000001]
["2017-04-15",3646.838817719879,1.03,7.1,17.8,0.3,7.03,17.399999999999999,null,null,null,null,null,null,12.4,0.8,7.1,17.8]
["2017-04-16",4253.4365271993302,1.05,7.04,17.600000000000001,0.27,7.04,17.7,null,null,null,null,null,null,11.5,0.71,7,17.399999999999999]
["2017-04-17",3770.0226961019844,0.54,7.02,18.2,0.28999999999999998,7.03,18.8,null,null,null,null,null,null,12.7,0.72,7.1,18.100000000000001]
["2017-04-18",4146.1724476172722,0.88,6.88,17.8,0.34,6.86,18,null,null,null,null,null,null,12.7,0.72,7.1,17.8]
["2017-04-19",3545.2233806673739,1.25,7.05,17.5,0.43,6.97,17.899999999999999,null,null,null,null,null,null,11.3,0.68,7,17.600000000000001]
["2017-04-20",3806.6082970435255,1,7,17.5,0.3,7.01,17.600000000000001,null,null,null,null,null,null,12.4,0.92,7.1,18]
["2017-04-21",3609.3224054594743,0.8,7.03,18,0.49,7.05,18,null,null,null,null,null,null,13.9,1.1399999999999999,7.1,17.600000000000001]
["2017-04-22",3913.5906281073699,0.9,7.03,17.7,0.3,7.05,17.899999999999999,null,null,null,null,null,null,12.6,1.17,7,17.399999999999999]
["2017-04-23",3478.4215200908748,0.96,7.17,18,0.4,7.19,18.100000000000001,null,null,null,null,null,null,10.9,1.1000000000000001,7.1,17.7]
["2017-04-24",4040.0436182231952,0.72,7.56,18,0.67,7.16,18.8,null,null,null,null,null,null,11.9,1.05,7.4,18.100000000000001]
["2017-04-25",4225.1108474508828,1.07,7.42,18.100000000000001,0.39,7.38,19,null,null,null,null,null,null,11.5,1.2,7.4,18.5]
["2017-04-26",3962.6453484697099,0.62,7.55,18.100000000000001,0.28999999999999998,7.48,18.5,null,null,null,null,null,null,10.199999999999999,1.22,7.4,18.3]
["2017-04-27",3987.7953461035322,0.79,7.63,18.600000000000001,0.47,7.59,18.3,null,null,null,null,null,null,14,1.17,7.6,18.2]
["2017-04-28",3452.3668661384759,0.68,7.5,18.2,0.32,7.48,18.3,null,null,null,null,null,null,12.1,1.17,7.5,18.8]
["2017-04-29",3720.6781647770131,0.52,7.48,18.5,0.42,7.47,18.5,null,null,null,null,null,null,9.9,1.1299999999999999,7.5,18.8]
["2017-04-30",3885.8082457236565,0.47,7.52,18.399999999999999,0.2,7.6,18.600000000000001,null,null,null,null,null,null,9.1999999999999993,1.2,7.5,18.899999999999999]
["2017-05-01",4157.0742197375675,0.71,7.4,18.399999999999999,0.39,7.38,18.5,null,null,null,null,null,null,10.5,1.2,7.4,18.399999999999999]
["2017-05-02",3809.1024050317183,0.41,7.46,19.3,0.22,7.48,19.3,null,null,null,null,null,null,13.4,1.1100000000000001,7.4,18.899999999999999]
["2017-05-03",3279.7532192460017,0.77,7.49,18.899999999999999,0.48,7.43,18.899999999999999,null,null,null,null,null,null,14.1,1.24,7.4,18.7]
["2017-05-04",3345.5769449933509,0.6,7.43,19.5,0.47,7.39,19.5,null,null,null,null,null,null,12.5,1.24,7.4,19]
["2017-05-05",3831.6020236326067,0.62,7.57,19.7,0.4,7.55,19.5,null,null,null,null,null,null,14.9,1.18,7.4,19.5]
["2017-05-06",4068.4406267727545,0.98,7.57,19.899999999999999,0.3,7.54,20.2,null,null,null,null,null,null,11.8,1.1499999999999999,7.4,20.2]
["2017-05-07",3298.3389784215437,0.7,7.46,20.399999999999999,0.2,7.51,20.3,null,null,null,null,null,null,9.6,1.1399999999999999,7.4,20.100000000000001]
["2017-05-08",4111.1071689989058,1.1299999999999999,7.45,20.399999999999999,0.57999999999999996,7.42,20.6,null,null,null,null,null,null,11.2,1.24,7.4,20.399999999999999]
["2017-05-09",3650.1397512286935,0.54,7.41,20.8,0.28999999999999998,7.41,20.8,null,null,null,null,null,null,11.6,1.2,7.4,21.1]
["2017-05-10",3575.9425407276594,0.26,7.57,22,0.2,7.4,21.8,null,null,null,null,null,null,13,0.93,7.5,21.3]
[{"$f":"A147+1","v":"2017-05-11"},4211.1432279143819,0.63,7.31,21.4,0.17,7.3,21.5,null,null,null,null,null,null,9.6,1.74,7.4,21.2]
["2017-05-12",3533.8628190909621,0.98899999999999999,7.5,21.4,0.19,7.49,21.5,null,null,null,null,null,null,13,1.85,7.4,21.4]
["2017-05-13",4174.1222630292541,0.31,7.4,21.4,0.46,7.43,21.5,null,null,null,null,null,null,9.3000000000000007,1.93,7.4,22]
["2017-05-14",3916.8490570468848,0.52,7.54,22.5,0.2,7.52,22.6,null,null,null,null,null,null,9.3000000000000007,1.76,7.5,21.6]
["2017-05-15",4344.3590906539821,0.65,7.27,22.4,0.4,7.27,22.2,null,null,null,null,null,null,11.6,1.62,7.4,22.4]
["2017-05-16",3357.458797654197,0.72,7.33,21.9,0.32,7.3,22.3,null,null,null,null,null,null,10.1,1.7,7.4,22.3]
["2017-05-17",3274.6477051492138,0.52,7.51,22.7,0.14000000000000001,7.55,22.8,null,null,null,null,null,null,14.9,1.27,7.6,22.7]
["2017-05-18",3775.2629854027077,0.33,7.36,22.8,0.21,7.36,22.9,null,null,null,null,null,null,12.6,1.47,7.4,22.8]
["2017-05-19",3371.3729005044975,0.4,7.32,22.3,0.19,7.48,23,null,null,null,null,null,null,14.9,1.44,7.4,22.6]
["2017-05-20",4281.0008108548118,0.3,7.37,22.5,0.37,7.43,22.9,null,null,null,null,null,null,11.1,1.5,7.4,23.1]
["2017-05-21",3872.6308408126793,0.48,7.34,23.4,0.27,7.35,23.5,null,null,null,null,null,null,13.1,1.46,7.4,23.3]
["2017-05-22",3587.3083369076576,0.56000000000000005,7.38,24.6,0.39,7.5,24.2,null,null,null,null,null,null,11,1.2,7.4,24.3]
["2017-05-23",3766.8443314621186,0.27,7.42,24.6,0.13,7.42,24.4,null,null,null,null,null,null,11.3,1.2,7.4,24]
["2017-05-24",3763.9168743770815,0.68,7.46,23.5,0.28999999999999998,7.43,23.9,null,null,null,null,null,null,11.7,1.2,7.5,23.9]
["2017-05-25",3409.203934788598,0.54,7.44,24,0.18,7.43,24.2,null,null,null,null,null,null,12.3,1.2,7.5,24.4]
["2017-05-26",4188.5357325824216,0.57999999999999996,7.43,24.4,0.28999999999999998,7.43,24.3,null,null,null,null,null,null,12.6,1.1599999999999999,7.5,24.5]
["2017-05-27",4195.6019350799243,0.45,7.41,24.9,0.2,7.43,25,null,null,null,null,null,null,13.9,1.1499999999999999,7.4,25]
["2017-05-28",3293.5759926165292,0.68,7.35,25,0.28000000000000003,7.46,24.4,null,null,null,null,null,null,11.8,1.2,7.5,24.4]
["2017-05-29",3841.4307300224659,0.28999999999999998,7.33,25.8,0.08,7.36,25.7,null,null,null,null,null,null,12.6,1.17,7.4,25.5]
["2017-05-30",4166.9397465106777,0.54,7.49,25,0.36,7.48,25.9,null,null,null,null,null,null,13.9,1.19,7.7,25.8]
["2017-05-31",3876.625160275174,0.99,7.58,25.9,0.36,7.48,26.2,null,null,null,null,null,null,11.7,1.1499999999999999,7.6,26.3]
["2017-06-01",3316.6542729574076,0.73,7.42,25.8,0.48,7.35,26.5,null,null,null,null,null,null,10.5,1.06,7.5,26.6]
["2017-06-02",3498.9168414294745,0.3,7.42,25.6,0.41,7.39,26,null,null,null,null,null,null,10.7,1.1200000000000001,7.4,25.8]
["2017-06-03",3716.5362422759968,0.2,7.39,25.7,0.21,7.39,25.6,null,null,null,null,null,null,10.9,1.1499999999999999,7.4,25.6]
["2017-06-04",3784.3213080881105,0.4,7.43,25.2,0.24,7.36,25.3,null,null,null,null,null,null,13.4,1.29,7.4,25.2]
["2017-06-05",3841.6689342054169,1.51,7.36,27.6,0.62,7.06,26.7,null,null,null,null,null,null,9.6,1.1299999999999999,7.5,25.9]
["2017-06-06",3765.2138915305077,0.74,7.32,25.6,0.34,7.39,26.3,null,null,null,null,null,null,11.4,1.1200000000000001,7.4,25.8]
["2017-06-07",3878.0469862199093,0.78,7.48,25.8,0.36,7.41,26.3,null,null,null,null,null,null,11,1.1499999999999999,7.6,26.2]
["2017-06-08",3479.7065134844256,0.85,7.75,23.6,0.15,7.4,26.4,null,null,null,null,null,null,14.5,1.07,7.6,26.2]
["2017-06-09",3826.8579559088735,0.18,7.48,25.8,0.32,7.53,26,null,null,null,null,null,null,11.8,1.06,7.5,26.4]
["2017-06-10",3290.3637711697224,0.85,7.69,26,0.39,7.54,26.1,null,null,null,null,null,null,10.6,1.18,7.6,26.3]
["2017-06-11",3723.340714237273,1.1120000000000001,7.54,26.5,0.39,7.44,26.4,null,null,null,null,null,null,10.9,1.21,7.5,26.4]
["2017-06-12",3885.8652384708444,1.35,7.44,26.5,0.34,7.46,26.6,null,null,null,null,null,null,11.9,1.2,7.5,26.6]
["2017-06-13",4013.0336504596216,0.76,7.36,26.9,0.13,7.41,26.9,null,null,null,null,null,null,12.6,1.18,7.4,26.2]
["2017-06-14",3593.913253881602,1.38,7.4,26.5,0.63,7.42,26.6,null,null,null,null,null,null,12.6,1.3,7.4,26.5]
["2017-06-15",4094.4291633580383,1.3,7.57,27,0.51,7.52,27,null,null,null,null,null,null,10.4,1.5,7.5,26.9]
["2017-06-16",3446.1405991494144,0.7,7.41,26.9,0.4,7.54,26.8,null,null,null,null,null,null,12.9,1.4,7.5,26.9]
["2017-06-17",3304.1928195129067,1.5,7.41,26.8,0.4,7.54,27.1,null,null,null,null,null,null,13.6,1.4,7.4,26.8]
["2017-06-18",4231.8316668088128,1.0900000000000001,7.52,26.7,0.57999999999999996,7.48,26.8,null,null,null,null,null,null,14.8,1.39,7.5,27.8]
["2017-06-19",4139.6806620123816,0.96,7.59,27.6,0.54,7.52,27.4,null,null,null,null,null,null,10.7,1.33,7.6,27]
["2017-06-20",3312.7367802144477,0.66,7.52,26.8,0.21,7.5,27,null,null,null,null,null,null,15.1,1.3,7.6,27.4]
["2017-06-21",3435.4077810376953,0.3,7.45,27.3,0.34,7.47,27.6,null,null,null,null,null,null,14.8,1.33,7.5,27.5]
["2017-06-22",3281.0434019289951,0.48,7.59,27.8,0.23,7.54,27.8,null,null,null,null,null,null,12.5,1.58,7.5,27.3]
["2017-06-23",4005.0955940259105,0.28999999999999998,7.42,27.5,0.15,7.44,27.6,null,null,null,null,null,null,12.2,1.68,7.4,27.4]
["2017-06-24",3312.4193526167705,0.81,7.29,27.1,0.09,7.39,22.5,null,null,null,null,null,null,16.100000000000001,1.73,7.5,27.4]
["2017-06-25",3994.0154001931901,0.9,7.36,27.8,0.18,7.41,28.1,null,null,null,null,null,null,13.3,1.62,7.4,27.8]
["2017-06-26",3950.3414608197772,1.36,7.55,27.5,0.3,7.5,28,null,null,null,null,null,null,12.6,1.76,7.4,27.8]
["2017-06-27",3912.6004552839072,1.05,7.5,27.4,0.28999999999999998,7.43,28.1,null,null,null,null,null,null,13.5,1.62,7.4,28.1]
["2017-06-28",3931.7783042306728,1.05,7.54,27,0.27,7.32,28.1,null,null,null,null,null,null,13.5,1.65,7.4,27.9]
["2017-06-29",3919.0089082376953,1.44,7.49,28.4,0.33,7.44,28.2,null,null,null,null,null,null,12,1.62,7.4,27.5]
["2017-06-30",3521.5481915304626,1.02,7.47,27.4,0.56000000000000005,7.4,28.2,null,null,null,null,null,null,14,1.64,7.4,27.6]
["2017-07-01",3288.8164762416122,1.04,7.43,28,0.2,7.41,27.8,null,null,null,null,null,null,12,0.66,7.4,27.9]
["2017-07-02",4096.5539612630337,3.2,7.42,27.6,1.4410000000000001,7.41,27.5,null,null,null,null,null,null,9.4,0.86,7.4,27.7]
["2017-07-03",3798.0521967109139,1.26,7.38,27.9,0.55000000000000004,7.42,27.8,null,null,null,null,null,null,13.2,1.56,7.4,27.9]
["2017-07-04",3321.1919703758876,1.24,7.37,27.4,0.56999999999999995,7.39,27.9,null,null,null,null,null,null,10.8,1.66,7.4,27.7]
["2017-07-05",3682.8204164435415,0.5,7.92,27.7,0.18,7.36,27.9,null,null,null,null,null,null,13.7,1.68,7.4,27.6]
["2017-07-06",4137.7679772377378,1.5,7.37,27.2,0.59,7.33,27.6,null,null,null,null,null,null,11.4,1.7,7.4,27.2]
["2017-07-07",4244.2956766897087,0.59,7.47,26.5,0.22,7.44,27.5,null,null,null,null,null,null,12.1,1.69,7.4,27.2]
["2017-07-08",4074.8258757160584,0.51,7.46,26.9,0.23,7.47,27.8,null,null,null,null,null,null,12.6,1.7,7.4,27.6]
["2017-07-09",3558.2455729047815,0.74,7.34,27,0.59,7.35,27,null,null,null,null,null,null,11.7,1.61,7.3,27.7]
["2017-07-10",3984.1604254649487,0.73,7.49,28.2,0.41,7.51,28.1,null,null,null,null,null,null,13.4,1.51,7.4,27.8]
["2017-07-11",3282.0470904288113,1.06,7.58,27.9,0.21,7.42,27.9,null,null,null,null,null,null,13.3,1.7,7.4,27.9]
["2017-07-12",4174.8731950465562,1.1200000000000001,7.34,27.6,0.53,7.46,27.6,null,null,null,null,null,null,13.9,1.53,7.4,27.6]
["2017-07-13",3899.0927817050742,1.1299999999999999,7.34,27.5,0.53,7.35,27.9,null,null,null,null,null,null,14.3,1.7,7.4,27.8]
[{"$f":"A211+1","v":"2017-07-14"},3526.5530742053566,0.9,7.31,27.5,0.27,7.36,27.8,null,null,null,null,null,null,12.9,1.7,7.3,28]
["2017-07-15",3946.936957121874,0.4,7.38,27.5,0.09,7.33,27.6,null,null,null,null,null,null,16.100000000000001,1.7,7.4,27.9]
["2017-07-16",3924.5433480569241,1.1100000000000001,7.47,28.1,0.56000000000000005,7.45,28.1,null,null,null,null,null,null,13.2,1.63,7.4,27.8]
["2017-07-17",4062.375440282116,1.08,7.54,28.2,0.52,7.52,28.1,null,null,null,null,null,null,15.2,1.6,7.6,28.5]
["2017-07-18",3909.1867313519388,0.81,7.39,28.2,0.38,7.39,28.1,null,null,null,null,null,null,9.3000000000000007,1.62,7.4,28]
["2017-07-19",4151.5343380145778,0.75,7.41,28.2,0.36,7.44,28.1,null,null,null,null,null,null,14.6,1.57,7.4,28.2]
["2017-07-20",3901.6816961694976,1.04,7.49,28.2,0.49,7.47,28.1,null,null,null,null,null,null,11.7,1.72,7.4,27.9]
["2017-07-21",3665.5797294926142,1.06,7.45,26.6,0.23,7.43,27.7,null,null,null,null,null,null,14.4,1.65,7.4,27.6]
["2017-07-22",3794.4346915642459,0.92,7.42,26.9,0.4,7.31,27.7,null,null,null,null,null,null,13.5,1.7,7.3,27.2]
["2017-07-23",3752.9409519297114,0.9,7.45,26.7,0.4,7.43,27.3,null,null,null,null,null,null,14.5,1.6,7.4,27.1]
["2017-07-24",3652.792379371157,0.7,7.39,27.4,0.3,7.32,27.6,null,null,null,null,null,null,12.9,1.7,7.4,27.1]
["2017-07-25",3739.7317659500391,1,7.35,26.7,0.27,7.36,26.9,null,null,null,null,null,null,12.5,1.6,7.4,27]
["2017-07-26",3766.3610915041763,0.53,7.48,26.3,0.18,7.38,26.6,null,null,null,null,null,null,14.7,1.67,7.4,26.8]
["2017-07-27",3425.4646641276272,1.1599999999999999,7.5,25.3,0.47,7.44,26.4,null,null,null,null,null,null,13.6,1.36,7.4,26.2]
["2017-07-28",4020.621212271983,0.68,7.49,26.1,0.3,7.31,26.4,null,null,null,null,null,null,14.1,1.59,7.3,26.1]
["2017-07-29",4084.3598557331761,1.02,7.39,26.5,0.3,7.48,26.7,null,null,null,null,null,null,13,1.54,7.4,26.1]
["2017-07-30",3302.1144492701114,1.07,7.4,26.2,0.32,7.44,26.1,null,null,null,null,null,null,10.9,1.67,7.4,26.1]
["2017-07-31",4227.6586120911952,1.32,7.45,25.8,0.46,7.42,25.9,null,null,null,null,null,null,11.8,1.73,7.4,25.8]
["2017-08-01",3841.6593322937179,1.3,7.36,25.6,0.21,7.32,26.4,null,null,null,null,null,null,10.7,0.5,7.4,25.9]
["2017-08-02",3273.0982188323997,0.82,7.56,26.6,0.26,7.47,26.6,null,null,null,null,null,null,9.6999999999999993,1.77,7.4,26.4]
["2017-08-03",3620.7721065776364,0.42,7.32,26.3,0.15,7.29,26.2,null,null,null,null,null,null,14.6,1.79,7.3,26.5]
["2017-08-04",3267.7113716238223,0.8,7.35,25.5,0.33,7.35,25.7,null,null,null,null,null,null,16.2,1.79,7.3,26.5]
["2017-08-05",3299.4072344206843,0.7,7.34,24.7,0.11,7.31,25.2,null,null,null,null,null,null,15.6,1.75,7.3,25.3]
["2017-08-06",3306.5607336429575,0.8,7.43,24.7,0.21,7.3,24.7,null,null,null,null,null,null,13.7,1.6,7.4,24.8]
["2017-08-07",3461.3901999926329,0.78,7.36,24.7,0.3,7.37,24.4,null,null,null,null,null,null,10.9,1.63,7.4,24.9]
["2017-08-08",3904.1327918842799,1.25,7.52,24.7,0.72,7.42,24.5,null,null,null,null,null,null,13.7,1.4,7.4,24.9]
["2017-08-09",3616.0588864722258,1.02,7.52,24.5,0.3,7.34,24.5,null,null,null,null,null,null,12.4,1.65,7.3,24.4]
["2017-08-10",4141.3342195097457,1.1100000000000001,7.28,23.8,0.34,7.29,24.5,null,null,null,null,null,null,12.6,1.65,7.4,24.1]
["2017-08-11",4081.7313991252345,0.59,7.32,23.8,0.34,7.34,24.1,null,null,null,null,null,null,11.7,1.78,7.3,24]
["2017-08-12",3658.6332427632751,0.53,7.42,23.2,0.09,7.41,23.7,null,null,null,null,null,null,11.3,1.64,7.4,24]
["2017-08-13",3780.8588098650139,1.17,7.39,24.4,0.52,7.34,24.3,null,null,null,null,null,null,12.5,1.6,7.3,23.9]
["2017-08-14",3398.5005030253405,1.21,7.42,23.5,0.13,7.36,23.4,null,null,null,null,null,null,15.5,1.72,7.3,23.8]
["2017-08-15",4342.5709620176549,1.17,7.42,23.6,0.45,7.37,23.4,null,null,null,null,null,null,15,1.8,7.4,23.8]
["2017-08-16",4322.8598677521886,1.1200000000000001,7.48,23.5,0.73,7.37,23.4,null,null,null,null,null,null,14.3,1.6,7.4,23.8]
["2017-08-17",4267.3679261614143,1.18,7.35,23.9,0.47,7.34,23.9,null,null,null,null,null,null,13.5,1.79,7.4,23.9]
["2017-08-18",3932.026166980856,1.07,7.33,23.4,0.2,7.33,23.7,null,null,null,null,null,null,11.5,1.69,7.4,23.7]
["2017-08-19",3796.7527291031497,0.78,7.29,23.7,0.3,7.34,23.6,null,null,null,null,null,null,12.6,1.74,7.3,23.8]
["2017-08-20",3808.5809823453942,0.23,7.39,23.8,0.08,7.26,23.6,null,null,null,null,null,null,14.9,1.67,7.4,23.9]
["2017-08-21",3299.22572202826,1.48,7.44,23.7,0.25,7.37,23.6,null,null,null,null,null,null,14.5,1.73,7.4,23.8]
["2017-08-22",3443.9273243092507,0.9,7.38,23.8,0.35,7.41,24,null,null,null,null,null,null,13.3,1.81,7.4,23.5]
["2017-08-23",3496.5126322662327,0.6,7.45,23.7,0.03,7.44,24.2,null,null,null,null,null,null,14,1.76,7.4,24.5]
["2017-08-24",4123.4467759183062,1,7.5,23.8,0.4,7.37,24.2,null,null,null,null,null,null,12.3,1.69,7.4,24.2]
["2017-08-25",3621.3924251088561,0.2,7.35,22.1,0.18,7.41,22.3,null,null,null,null,null,null,16.5,1.8,7.4,22.6]
["2017-08-26",4172.5013851455715,0.2,7.53,22.5,0.32,7.41,22.5,null,null,null,null,null,null,16.2,1.78,7.4,23.7]
["2017-08-27",3302.9403145193155,0.77,7.43,23.1,0.56999999999999995,7.37,22.9,null,null,null,null,null,null,13.5,1.7,7.4,23.4]
["2017-08-28",3587.6192979501179,0.55000000000000004,7.47,22.7,0.32,7.39,23,null,null,null,null,null,null,14.4,1.64,7.4,22.5]
["2017-08-29",3443.4248728013813,1.1399999999999999,7.46,22,0.37,7.39,22.1,null,null,null,null,null,null,11,1.69,7.4,22.1]
["2017-08-30",3554.3872311923674,1.06,7.46,21.8,0.42,7.39,21.9,null,null,null,null,null,null,15.3,1.64,7.4,21.9]
["2017-08-31",4031.7456672268868,1.19,7.31,21.8,0.62,7.27,22.2,null,null,null,null,null,null,15.3,1.6,7.3,22]
["2017-09-01",3638.6960442332784,1.1499999999999999,7.38,21.3,0.42,7.39,21.4,null,null,null,null,null,null,14.5,1.7,7.3,21.4]
["2017-09-02",4074.4223194962065,1.33,7.42,20.5,0.41,7.4,20.8,null,null,null,null,null,null,14.8,1.7,7.3,20.8]
["2017-09-03",3821.539739882895,0.97,7.47,20.2,0.54,7.39,20.3,null,null,null,null,null,null,14.7,1.58,7.3,20.100000000000001]
["2017-09-04",3530.9449852410808,0.41,7.28,19.2,0.09,7.25,19.3,null,null,null,null,null,null,15.5,1.69,7.3,19.399999999999999]
["2017-09-05",3703.8674882411065,1.37,7.52,18.899999999999999,0.37,7.44,19.100000000000001,null,null,null,null,null,null,13.6,1.19,7.4,19.2]
["2017-09-06",4296.3861512895401,1.06,7.29,19.2,0.48,7.29,19.100000000000001,null,null,null,null,null,null,14.9,1.75,7.3,18.7]
["2017-09-07",4188.1254975095535,1.23,7.5,18.600000000000001,0.56999999999999995,7.49,18.600000000000001,null,null,null,null,null,null,12.5,1.71,7.4,18.600000000000001]
["2017-09-08",3510.5144077069208,0.94,7.29,18.899999999999999,0.44,7.38,18.8,null,null,null,null,null,null,12.7,1.69,7.3,18.7]
["2017-09-09",3842.2944096638635,0.94,7.47,19.2,0.48,7.39,19.100000000000001,null,null,null,null,null,null,12.8,1.67,7.4,18.7]
["2017-09-10",3559.8749773311142,1.2,7.43,19.100000000000001,0.46,7.43,18.899999999999999,null,null,null,null,null,null,15.7,1.77,7.4,18.600000000000001]
["2017-09-11",3370.5287124042179,0.51,7.49,18.899999999999999,0.45,7.32,19,null,null,null,null,null,null,10.9,1.84,7.3,18.8]
["2017-09-12",3385.3444053732287,0.51,7.49,18.8,0.24,7.39,19,null,null,null,null,null,null,13.4,1.68,7.4,19.100000000000001]
["2017-09-13",3571.7573707916031,1,7.46,18.5,0.4,7.43,18.7,null,null,null,null,null,null,13,1.7,7.4,18.8]
["2017-09-14",3605.4184396674223,0.9,7.6,18.8,0.68,7.43,18.899999999999999,null,null,null,null,null,null,13.9,1.8,7.4,18.7]
["2017-09-15",3473.3652317749111,1.1000000000000001,7.4,18.399999999999999,0.31,7.45,18.399999999999999,null,null,null,null,null,null,15.6,1.8,7.4,18.100000000000001]
[{"$f":"A275+1","v":"2017-09-16"},3443.3998491687566,0.9,7.38,17.399999999999999,0.28999999999999998,7.46,17.5,null,null,null,null,null,null,13.8,1.7,7.4,17.600000000000001]
["2017-09-17",3302.0445320507488,0.96,7.5,17.600000000000001,0.54,7.35,17.600000000000001,null,null,null,null,null,null,12.7,1.7,7.4,18]
["2017-09-18",3371.5144282471892,1.1200000000000001,7.42,18,0.28999999999999998,7.3,18.100000000000001,null,null,null,null,null,null,16.3,1.66,7.4,18.100000000000001]
["2017-09-19",3650.6704120412237,1.21,7.49,17.5,0.54,7.45,17.7,null,null,null,null,null,null,13.8,1.7,7.4,17.600000000000001]
["2017-09-20",3841.8116835830456,0.94,7.29,17.7,0.51,7.29,17.7,null,null,null,null,null,null,14.7,1.6,7.3,17.7]
["2017-09-21",4056.9917725730188,0.79,7.52,17.3,0.33,7.44,17.2,null,null,null,null,null,null,13.7,1.63,7.5,17.399999999999999]
["2017-09-22",4298.9749768539832,0.57999999999999996,7.4,16.600000000000001,0.16,7.45,16.600000000000001,null,null,null,null,null,null,14.5,1.62,7.4,17.100000000000001]
["2017-09-23",3262.3261450788982,0.98,7.4,17.3,0.35,7.49,16.7,null,null,null,null,null,null,11.1,1.68,7.4,17.3]
["2017-09-24",3647.282731070758,0.88,7.59,17,0.41,7.56,17,null,null,null,null,null,null,14,1.78,7.4,17.100000000000001]
["2017-09-25",3407.0479377371971,0.78,7.39,17.2,0.61,7.36,17.2,null,null,null,null,null,null,13.6,1.7,7.4,16.899999999999999]
["2017-09-26",3914.2379188749032,0.82,7.47,17.2,0.32,7.39,17.100000000000001,null,null,null,null,null,null,12.9,1.64,7.4,16.8]
["2017-09-27",3512.7489327810522,0.88,7.45,17.100000000000001,0.4,7.39,17,null,null,null,null,null,null,14.3,1.71,7.4,16.899999999999999]
["2017-09-28",3329.4072711838317,1.02,7.46,16.2,0.48,7.43,16.600000000000001,null,null,null,null,null,null,12.8,1.1299999999999999,7.4,16.600000000000001]
["2017-09-29",3674.7741421393289,0.72,7.47,16.600000000000001,0.13,7.39,16.7,null,null,null,null,null,null,13,1.23,7.4,16]
["2017-09-30",3548.0734791928567,0.78,7.31,15.9,0.4,7.32,16,null,null,null,null,null,null,13.8,1.47,7.4,15.7]
["2017-10-01",3749.9405368624493,0.91,7.37,15.8,0.4,7.42,16.2,null,null,null,null,null,null,15.1,1.38,7.4,15.7]
["2017-10-02",4025.1705064690614,0.77,7.57,15.5,0.43,7.37,15.6,null,null,null,null,null,null,12.6,1.32,7.4,15.5]
["2017-10-03",3877.6476992358339,0.9,7.47,15.4,0.22,7.43,15.3,null,null,null,null,null,null,15.3,1.19,7.4,16.100000000000001]
["2017-10-04",3969.969517741155,0.31,7.46,14.7,0.14000000000000001,7.43,15.2,null,null,null,null,null,null,14.7,1.17,7.4,14.4]
["2017-10-05",3595.5043503741986,0.4,7.47,14.8,0.28999999999999998,7.42,14.9,null,null,null,null,null,null,14,1.1000000000000001,7.4,15]
["2017-10-06",3668.0490518105848,0.4,7.5,14.5,0.28999999999999998,7.47,14.3,null,null,null,null,null,null,14,1.1499999999999999,7.4,14]
["2017-10-07",4219.7183396263245,0.1,7.44,13.4,0.25,7.43,13.4,null,null,null,null,null,null,12.1,1.1299999999999999,7.4,12.9]
["2017-10-08",3343.05459601759,0.76,7.47,13.1,0.28999999999999998,7.39,13,null,null,null,null,null,null,14.3,1.21,7.4,12.8]
["2017-10-09",3512.3863617470793,0.74,7.51,12.9,0.41,7.42,12.9,null,null,null,null,null,null,13.2,1.06,7.4,12.8]
["2017-10-10",3781.0391062659278,0.67,7.47,13.1,0.37,7.41,13,null,null,null,null,null,null,12.2,1.0900000000000001,7.4,13]
["2017-10-11",3281.8943323159692,0.64,7.44,12.7,0.24,7.4,12.9,null,null,null,null,null,null,11,1.2,7.4,13]
["2017-10-12",3811.2001101789228,0.69,7.49,13.1,0.44,7.41,13,null,null,null,null,null,null,10.9,1.2,7.5,12.8]
["2017-10-13",3964.6521763100122,0.46,7.44,13.1,0.28000000000000003,7.52,12.6,null,null,null,null,null,null,10.5,1.36,7.5,13.1]
["2017-10-14",3363.8317806807236,0.59,7.72,12.9,0.34,7.34,12.7,null,null,null,null,null,null,10.5,1.34,8,13.3]
["2017-10-15",3498.8034291878366,0.48,7.46,12.9,0.31,7.39,12.8,null,null,null,null,null,null,10.5,1.2,7.5,12.8]
["2017-10-16",3473.2878356607898,0.54,7.39,12.8,0.36,7.32,12.8,null,null,null,null,null,null,13.1,1.3,7.4,12.5]
["2017-10-17",3709.8090533507934,0.36,7.43,12.4,0.16,7.41,12.3,null,null,null,null,null,null,12.2,1.35,7.5,12.3]
["2017-10-18",3819.0517241552593,0.68,7.37,11.9,0.28999999999999998,7.34,11.8,null,null,null,null,null,null,9.5,1.24,7.4,11.9]
["2017-10-19",3469.5726306481442,0.8,7.2,12.7,0.36,7.22,12.1,null,null,null,null,null,null,13.2,1.4,7.4,12]
["2017-10-20",3679.3925266874812,0.62,7.41,11.9,0.28000000000000003,7.41,11.8,null,null,null,null,null,null,11.4,1.4,7.4,11.5]
["2017-10-21",3466.9368135682066,0.59,7.46,12,0.36699999999999999,7.41,11.9,null,null,null,null,null,null,14.5,1.21,7.4,11.2]
["2017-10-22",3816.9056427056084,2.74,7.34,12.5,2.0499999999999998,7.31,12.1,null,null,null,null,null,null,15.2,1.1399999999999999,7.4,11.9]
["2017-10-23",4233.2601216371686,0.49,7.47,13.9,0.13,7.46,13.4,null,null,null,null,null,null,12.9,1.33,7.4,13.4]
["2017-10-24",3436.8418995542493,0.55000000000000004,7.47,13.5,0.3,7.46,13.4,null,null,null,null,null,null,13.6,1.34,7.4,13.2]
["2017-10-25",3827.5643892925955,0.17,7.44,12.5,0.15,7.34,12.3,null,null,null,null,null,null,12.5,1.19,7.4,12.3]
["2017-10-26",3920.806996646169,0.31,7.36,12.8,0.17,7.21,12.2,null,null,null,null,null,null,12.8,1.35,7.4,12]
["2017-10-27",3293.7121745821737,0.4,7.41,12,0.21,7.34,12.1,null,null,null,null,null,null,13.8,1.26,7.4,11.1]
["2017-10-28",3544.7758918631907,0.4,7.37,11.5,0.08,7.35,11.4,null,null,null,null,null,null,13.8,1.3,7.3,10.6]
["2017-10-29",3574.5660201005153,0.33,7.48,11.8,0.24,7.46,11.4,null,null,null,null,null,null,14.5,1.2,7.4,11]
["2017-10-30",3811.582818011404,0.42,7.44,11.5,0.14000000000000001,7.39,11.3,null,null,null,null,null,null,12,1.1100000000000001,7.4,11.2]
["2017-10-31",4245.2773275394147,0.62,7.45,10.7,0.36,7.39,11.3,null,null,null,null,null,null,12.4,1.25,7.4,10.6]
["2017-11-01",3335.773378752981,0.28000000000000003,7.45,10.9,0.15,7.4,10.9,null,null,null,null,null,null,12.1,1.22,7.4,10.4]
["2017-11-02",3485.2498376363346,0.34,7.47,10.199999999999999,0.28000000000000003,7.42,10.1,null,null,null,null,null,null,13.5,1.35,7.4,9.8000000000000007]
["2017-11-03",3854.3006599120245,0.48,7.54,9.6999999999999993,0.3,7.32,9.5,null,null,null,null,null,null,11.2,1.36,7.4,9.8000000000000007]
["2017-11-04",4123.803694716421,0.42,7.52,10,0.33,7.41,9.1,null,null,null,null,null,null,12.2,1.3,7.5,9.4]
["2017-11-05",3733.0089050414895,1.1299999999999999,7.49,9.8000000000000007,0.65,7.41,9.6,null,null,null,null,null,null,15,1.5,7.5,8.9]
["2017-11-06",4191.390678376928,1.32,7.53,9.1999999999999993,0.71,7.61,8.4,null,null,null,null,null,null,13.8,1.4,7.6,8.1]
["2017-11-07",4224.9798243237028,1.3,7.44,8.6999999999999993,0.93,7.37,8.6,null,null,null,null,null,null,14.6,1.37,7.4,7.9]
["2017-11-08",3405.4834439078772,1,7.45,8,0.87,7.41,7.7,null,null,null,null,null,null,13,1.3,7.5,7.5]
["2017-11-09",3346.4736144296921,0.7,7.47,8.3000000000000007,0.6,7.43,7.7,null,null,null,null,null,null,13.7,1.3,7.5,7]
["2017-11-10",3326.8947406625957,0.98,7.39,7.4,0.8,7.41,7.3,null,null,null,null,null,null,14,1.4,7.5,7.1]
["2017-11-11",3805.3606740747528,1.1000000000000001,7.37,7.9,1.05,7.29,7.8,null,null,null,null,null,null,11.6,1.28,7.5,6.6]
["2017-11-12",3263.0239621027004,0.81,7.32,7,0.63,7.42,7,null,null,null,null,null,null,14.2,1.1599999999999999,7.5,6.6]
["2017-11-13",4086.2286842629305,0.89,7.32,6.8,0.69,7.33,6.9,null,null,null,null,null,null,13.1,1.26,7.6,6.2]
["2017-11-14",3940.7191081838332,0.88,7.34,6.6,0.84,7.35,6.5,null,null,null,null,null,null,13.2,1.24,7.4,6.2]
["2017-11-15",3443.2500182151734,1.01,7.35,6.5,0.7,7.3,6.4,null,null,null,null,null,null,12.9,1.04,7.4,5.6]
["2017-11-16",4031.135726122598,1.1599999999999999,7.29,6,0.78,7.34,6.4,null,null,null,null,null,null,12.2,1.18,7.4,6]
["2017-11-17",3560.9713292679089,1.3,7.38,6.1,0.9,7.28,6.1,null,null,null,null,null,null,10.4,1.3,7.4,6.2]
["2017-11-18",3663.3193055066008,1,7.35,6.1,0.82,7.32,6.3,null,null,null,null,null,null,12.7,1.2,7.4,5.0999999999999996]
[{"$f":"A339+1","v":"2017-11-19"},3600.6532789728294,1.01,7.48,5.2,0.8,7.42,5.4,null,null,null,null,null,null,14.4,1.2,7.6,5.4]
["2017-11-20",4318.528971556354,0.95,7.41,5.9,0.66,7.36,5.8,null,null,null,null,null,null,10.3,1.18,7.5,5.7]
["2017-11-21",3784.8860418008035,0.66,7.46,5.8,0.59,7.34,5.8,null,null,null,null,null,null,11.4,1,7.5,5.4]
["2017-11-22",4260.0318745750064,1.74,7.47,5.8,1.34,7.41,5.7,null,null,null,null,null,null,12.9,1.03,7.6,5.3]
["2017-11-23",3420.8736663504346,1.02,7.39,5.4,0.82,7.37,4.8,null,null,null,null,null,null,11,1.2,7.6,4.5]
["2017-11-24",4333.95926489266,1.1200000000000001,7.58,5.3,0.74,7.48,4.8,null,null,null,null,null,null,13,1.06,7.6,4.4000000000000004]
["2017-11-25",3773.9573780802975,0.84,7.51,5.0999999999999996,0.48,7.45,5.2,null,null,null,null,null,null,13.2,1.2,7.5,4.8]
["2017-11-26",3516.3646089073659,1,7.41,5.6,0.32,7.4,5.5,null,null,null,null,null,null,14.2,0.81,7.5,4.8]
["2017-11-27",3580.428730935143,1,7.54,5.0999999999999996,0.53,7.53,5.3,null,null,null,null,null,null,14.7,1.22,7.6,4.8]
["2017-11-28",3282.123793338923,1.01,7.56,5.3,0.88,7.53,5.7,null,null,null,null,null,null,14.2,1.2,7.6,4.7]
["2017-11-29",3441.6053971419278,1,7.69,5.7,0.83,7.72,5.9,null,null,null,null,null,null,12.7,1.19,7.8,4.4000000000000004]
["2017-11-30",3919.6337978349225,0.63,7.62,5.0999999999999996,0.6,7.54,5,null,null,null,null,null,null,13.8,1.2,7.6,5.0999999999999996]
["2017-12-01",3426.7072872411595,0.87,7.59,6.2,0.61,7.55,6,null,null,null,null,null,null,13.9,1.06,7.7,5.4]
["2017-12-02",3687.0666664737919,1.02,7.62,6,1.01,7.54,5.8,null,null,null,null,null,null,14.9,1.1100000000000001,7.7,5.4]
["2017-12-03",3940.3066194354506,1.1000000000000001,7.71,5.0999999999999996,0.8,7.74,6,null,null,null,null,null,null,12.8,1.2,7.7,5.6]
["2017-12-04",3292.7748958081156,1.7,8.4700000000000006,6.2,1.1000000000000001,8.15,6,null,null,null,null,null,null,13.4,1.2,8.1999999999999993,6.3]
["2017-12-05",3369.7867444015465,0.9,7.59,5.7,0.69,7.39,5.9,null,null,null,null,null,null,13.5,1.06,7.7,5.7]
["2017-12-06",4348.3392408583231,0.8,7.6,6.4,0.68,7.56,6,null,null,null,null,null,null,14.8,1,7.7,5.6]
["2017-12-07",3529.3340664444736,1.01,7.64,6,0.82,7.61,5.8,null,null,null,null,null,null,14.1,0.92,7.6,5.5]
["2017-12-08",3287.8799839107942,0.1,7.47,5.5,0.28999999999999998,7.57,5.6,null,null,null,null,null,null,15.3,1.17,7.6,4.2]
["2017-12-09",3735.2299290715691,0.6,7.51,5.2,0.35,7.47,5.5,null,null,null,null,null,null,14.4,1.2,7.5,4.2]
["2017-12-10",3981.7222733143976,0.3,7.69,5.4,0.24,7.62,5.0999999999999996,null,null,null,null,null,null,11.9,0.96,7.7,5]
["2017-12-11",3967.4018505239801,0.42,7.47,5.8,0.36,7.54,5.6,null,null,null,null,null,null,8.5,0.78,7.7,5]
["2017-12-12",3674.5624367730038,0.32,7.62,5.6,0.17,7.57,5.5,null,null,null,null,null,null,10.4,0.69,7.5,5.0999999999999996]
["2017-12-13",4063.5701566046537,0.1,7.57,6,0.12,7.53,6.4,null,null,null,null,null,null,13.4,0.98,7.5,5.9]
["2017-12-14",4320.9411103074572,0.62,7.61,5.4,0.28000000000000003,7.54,5.3,null,null,null,null,null,null,11.7,0.97,7.5,5.2]
["2017-12-15",3883.6904822796309,0.43,7.77,5.4,0.13,7.47,6,null,null,null,null,null,null,12.6,0.87,7.6,5]
["2017-12-16",3688.2821300286264,0.28000000000000003,7.5,6.9,0.16,7.51,5.4,null,null,null,null,null,null,14,0.94,7.6,5.5]
["2017-12-17",3957.4280193772579,0.35,7.62,5.7,0.17,7.49,5.7,null,null,null,null,null,null,14.7,1,7.5,5.7]
["2017-12-18",4095.7206119704365,0.33,7.65,6.5,0.17,7.62,6.7,null,null,null,null,null,null,13.8,0.93,7.6,6.1]
["2017-12-19",4111.108414081611,0.5,7.64,5.4,0.2,7.63,6.5,null,null,null,null,null,null,12.3,0.94,7.6,5]
["2017-12-20",4063.9378890083321,0.55000000000000004,7.54,5.5,0.34,7.57,5.4,null,null,null,null,null,null,14,0.91,8,5.0999999999999996]
["2017-12-21",4277.8527928340209,0.3,7.66,5.9,0.16,7.53,5.9,null,null,null,null,null,null,14.2,0.9,7.6,6]
["2017-12-22",4126.6019820870724,0.69,7.56,5.6,0.33,7.51,5.7,null,null,null,null,null,null,12.4,1,7.6,5]
["2017-12-23",3647.0338516895736,0.34,7.49,5.8,0.3,7.46,5.7,null,null,null,null,null,null,12.6,1,7.6,5]
["2017-12-24",4200.6073045854364,0.38,7.48,5.7,0.35,7.44,6.1,null,null,null,null,null,null,13.3,0.98,8,5.0999999999999996]
["2017-12-25",3850.8194897162693,0.4,7.54,6.3,0.15,7.47,6.6,null,null,null,null,null,null,15.8,0.92,7.6,4.5]
["2017-12-26",4080.3616655779674,0.43,7.65,6.1,0.22,7.55,6.4,null,null,null,null,null,null,14.3,0.94,7.6,4.5999999999999996]
["2017-12-27",3663.5809298183503,0.49,7.64,5.7,0.2,7.5,6.2,null,null,null,null,null,null,13.1,0.93,7.6,4.7]
["2017-12-28",4314.5664912142283,0.43,7.58,6.6,0.15,7.47,6.4,null,null,null,null,null,null,14,0.93,8,5.0999999999999996]
["2017-12-29",3686.0728090181319,0.4,7.54,6,0.3,7.59,6.4,null,null,null,null,null,null,16.5,0.9,7.6,4.4000000000000004]
["2017-12-30",4299.5454123177169,0.4,7.49,5.8,0.2,7.48,6.2,null,null,null,null,null,null,14.6,0.99,7.7,4.7]
["2017-12-31",4193.7655586285928,0.32,7.62,6.2,0.11,7.5,6.3,null,null,null,null,null,null,13.5,0.85,7.5,5.9]
["2018-01-01"]
[null,null,null,null,null,null,null,null,1.35,7.3,20]

{"sheet":"DataEntryValues(CT)","index":9,"n_rows":399,"n_cols":51,"rows_kept":399,"cut":false,"hidden":true,"merged":[[8,5,8,7],[11,5,11,7],[14,5,14,7],[27,2,27,4],[27,5,27,7],[16,5,16,7],[18,5,18,7],[2,5,2,7],[3,5,3,7],[6,5,6,7],[7,5,7,7],[5,5,5,7],[4,5,4,7],[27,11,27,13],[19,5,19,7],[9,5,9,7],[10,5,10,7],[12,5,12,7],[15,5,15,7],[13,5,13,7],[17,5,17,7],[27,8,27,10]]}
[]
[]
[null,"Plant Name",null,null,null,"Watertown",null,null,null,null,null,null,null,null,"T10/T factors >>>>>>>>>>>"]
[null,"Giardia Inactivation Requirement (log)"]
[null,"Giardia Inactivation Goal/Target (log)"]
[null,"Segment 1 Name"]
[null,"Segment 1 Volume (gal)"]
[null,"Segment 1 Factor"]
[null,"Segment 2 Name"]
[null,"Segment 2 Volume (gal)"]
[null,"Segment 2 Factor"]
[null,"Segment 3 Name"]
[null,"Segment 3 Volume (gal)"]
[null,"Segment 3 Factor"]
[null,"Segment 4 Name"]
[null,"Segment 4 Volume (gal)"]
[null,"Segment 4 Factor"]
[null,"Segment 5 Name"]
[null,"Segment 5 Volume (gal/ft)"]
[null,"Segment 5 Factor"]
[]
[null,"Instruction to users:  Input plant name, inactivation target, basin volumes, and baffle factors above.  Input start date"]
[null,"and data below.  The database will hold 366 days of data.  Following data input, update the summary report by clicking"]
[null,"the UPDATE button."]
[]
[]
["Data Entry Area for Posting Individual Values",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Log Inact","Goal",null,"M/R","M/R"]
[null,null,{"$f":"CONCATENATE(\"Segment 1 - \",$F$6)","v":"Segment 1 - "},null,null,{"$f":"CONCATENATE(\"Segment 2 - \",$F$9)","v":"Segment 2 - "},null,null,{"$f":"CONCATENATE(\"Segment 3 - \",$F$12)","v":"Segment 3 - "},null,null,{"$f":"CONCATENATE(\"Segment 4 - \",$F$15)","v":"Segment 4 - "},null,null,{"$f":"CONCATENATE(\"Segment 5 - \",$F$18)","v":"Segment 5 - "},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Plotting Values",null,null,null,"No Function",null,null,null,"Req'd","(log inact)",null,"Req'd","Goal"]
["Date","Flow","Residual","pH","Temp.","Residual","pH","Temp.","Residual","pH","Temp.","Residual","pH","Temp.","Depth","Residual","pH","Temp.",null,null,"Seg1 CT-M","Seg1 CT-R","Seg1 Ratio","Seg2 CT-M","Seg2 CT-R","Seg2 Ratio","Seg3 CT-M","Seg3 CT-R","Seg3 Ratio","Seg4 CT M","Seg4 CT R","Seg4 Ratio","Seg5 CT M","Seg5 CT R","Seg5 Ratio","Total Ratio","Total Inact.",null,"Inactivation Ratio","Giardia Inactivation",null,null,"CombSort",null,"Comb%",null,{"$f":"+Target","v":0},{"$f":"IF($F$5>0,$F$5,2*AU29)","v":0},null,{"$f":"+AU29/Target","v":{"$error":"#DIV/0!"}},{"$f":"+AV29/Target","v":{"$error":"#DIV/0!"}}]
[null,"gpm","mg/L",null,"C","mg/L",null,"C","mg/L",null,"C","mg/L",null,"C","ft","mg/L",null,"C",null,null,"mg/L-min","mg/L-min","M/R","mg/L-min","mg/L-min","M/R","mg/L-min","mg/L-min","M/R","mg/L-min","mg/L-min","M/R","mg/L-min","mg/L-min","M/R","M/R","Log",null,"M/R","Log"]
["2017-01-01",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,{"$f":"IF(B31=\"\",,Seg1Vol*Seg1Fac/B31*C31)","v":0},{"$f":"Target*0.2828*D31^2.69*C31^0.15*0.933^(E31-5)","v":0},{"$f":"IF(V31=0,,U31/V31)","v":0},{"$f":"IF(B31=\"\",,Seg2Vol*Seg2Fac/B31*F31)","v":0},{"$f":"Target*0.2828*G31^2.69*F31^0.15*0.933^(H31-5)","v":0},{"$f":"IF(Y31=0,,X31/Y31)","v":0},{"$f":"IF(B31=\"\",,Seg3Vol*Seg3Fac/B31*I31)","v":0},{"$f":"Target*0.2828*J31^2.69*I31^0.15*0.933^(K31-5)","v":0},{"$f":"IF(AB31=0,,AA31/AB31)","v":0},{"$f":"IF(B31=\"\",,Seg4Vol*Seg4Fac/B31*L31)","v":0},{"$f":"Target*0.2828*M31^2.69*L31^0.15*0.933^(N31-5)","v":0},{"$f":"IF(AE31=0,,AD31/AE31)","v":0},{"$f":"IF(B31=\"\",,Seg5Vol*O31*Seg5Fac/B31*P31)","v":0},{"$f":"Target*0.2828*Q31^2.69*P31^0.15*0.933^(R31-5)","v":0},{"$f":"IF(AH31=0,,AG31/AH31)","v":0},{"$f":"W31+Z31+AC31+AF31+AI31","v":0},{"$f":"AJ31*Target","v":0},null,4.2644760838270237,4.2644760838270237,null,null,18.78294941475,98,{"$f":"100*COUNT($AQ$31:AQ31)/$AQ$397","v":0.32362459546925565},null,{"$f":"$AU$29","v":0},{"$f":"+$AV$29","v":0},null,{"$f":"$AX$29","v":{"$error":"#DIV/0!"}},{"$f":"+$AY$29","v":{"$error":"#DIV/0!"}}]
[{"$f":"A31+1","v":"2017-01-02"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"T31+1","v":2},{"$f":"IF(B32=\"\",,Seg1Vol*Seg1Fac/B32*C32)","v":0},{"$f":"Target*0.2828*D32^2.69*C32^0.15*0.933^(E32-5)","v":0},{"$f":"IF(V32=0,,U32/V32)","v":0},{"$f":"IF(B32=\"\",,Seg2Vol*Seg2Fac/B32*F32)","v":0},{"$f":"Target*0.2828*G32^2.69*F32^0.15*0.933^(H32-5)","v":0},{"$f":"IF(Y32=0,,X32/Y32)","v":0},{"$f":"IF(B32=\"\",,Seg3Vol*Seg3Fac/B32*I32)","v":0},{"$f":"Target*0.2828*J32^2.69*I32^0.15*0.933^(K32-5)","v":0},{"$f":"IF(AB32=0,,AA32/AB32)","v":0},{"$f":"IF(B32=\"\",,Seg4Vol*Seg4Fac/B32*L32)","v":0},{"$f":"Target*0.2828*M32^2.69*L32^0.15*0.933^(N32-5)","v":0},{"$f":"IF(AE32=0,,AD32/AE32)","v":0},{"$f":"IF(B32=\"\",,Seg5Vol*O32*Seg5Fac/B32*P32)","v":0},{"$f":"Target*0.2828*Q32^2.69*P32^0.15*0.933^(R32-5)","v":0},{"$f":"IF(AH32=0,,AG32/AH32)","v":0},{"$f":"W32+Z32+AC32+AF32+AI32","v":0},{"$f":"AJ32*Target","v":0},null,5.5147699955998215,5.5147699955998215,null,null,12.934257597447001,50,{"$f":"100*COUNT($AQ$31:AQ32)/$AQ$397","v":0.6472491909385113},null,{"$f":"$AU$29","v":0},{"$f":"+$AV$29","v":0},null,{"$f":"$AX$29","v":{"$error":"#DIV/0!"}},{"$f":"+$AY$29","v":{"$error":"#DIV/0!"}}]
["2017-01-03",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,4.8935063243125612,4.8935063243125612,null,null,11.867157516177,291,{"$f":"100*COUNT($AQ$31:AQ33)/$AQ$397","v":0.970873786407767},null,0,0,null,{"$f":"$AX$29","v":{"$error":"#DIV/0!"}},{"$f":"+$AY$29","v":{"$error":"#DIV/0!"}}]
["2017-01-04",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.1671576252193034,5.1671576252193034,null,null,5.4983471596189997,181,{"$f":"100*COUNT($AQ$31:AQ34)/$AQ$397","v":1.2944983818770226},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-01-05",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.4791737364652633,5.4791737364652633,null,null,5.4613711989373002,343,{"$f":"100*COUNT($AQ$31:AQ35)/$AQ$397","v":1.6181229773462784},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-01-06",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,4.8758242586225542,4.8758242586225542,null,null,5.4317693574490002,47,{"$f":"100*COUNT($AQ$31:AQ36)/$AQ$397","v":1.941747572815534},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-01-07",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.3084465948729402,5.3084465948729402,null,null,5.3114926973331,99,{"$f":"100*COUNT($AQ$31:AQ37)/$AQ$397","v":2.2653721682847898},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-01-08",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,4.4101734370225936,4.4101734370225936,null,null,5.2866445414376004,208,{"$f":"100*COUNT($AQ$31:AQ38)/$AQ$397","v":2.5889967637540452},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-01-09",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,3.8832578902629686,3.8832578902629686,null,null,5.2375713634869996,125,{"$f":"100*COUNT($AQ$31:AQ39)/$AQ$397","v":2.912621359223301},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-01-10",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,4.5729938010180868,4.5729938010180868,null,null,5.1588398336137944,143,{"$f":"100*COUNT($AQ$31:AQ40)/$AQ$397","v":3.2362459546925568},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-01-11",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,11,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,4.5324212974041105,4.5324212974041105,null,null,5.1525435255929999,43,{"$f":"100*COUNT($AQ$31:AQ41)/$AQ$397","v":3.5598705501618122},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-01-12",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,4.4652464477546019,4.4652464477546019,null,null,4.9215462189986257,187,{"$f":"100*COUNT($AQ$31:AQ42)/$AQ$397","v":3.883495145631068},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-01-13",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,13,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.0181671609917506,5.0181671609917506,null,null,4.8981646863465418,211,{"$f":"100*COUNT($AQ$31:AQ43)/$AQ$397","v":4.2071197411003238},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-01-14",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,14,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,4.8044261622927014,4.8044261622927014,null,null,4.8758251966149997,162,{"$f":"100*COUNT($AQ$31:AQ44)/$AQ$397","v":4.5307443365695796},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-01-15",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,15,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,4.2495810664367859,4.2495810664367859,null,null,4.8643133911445622,228,{"$f":"100*COUNT($AQ$31:AQ45)/$AQ$397","v":4.8543689320388346},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-01-16",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,16,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.870102316544564,5.870102316544564,null,null,4.8528228218238656,191,{"$f":"100*COUNT($AQ$31:AQ46)/$AQ$397","v":5.1779935275080904},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-01-17",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,17,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.4889138100723756,5.4889138100723756,null,null,4.8326864495880004,116,{"$f":"100*COUNT($AQ$31:AQ47)/$AQ$397","v":5.5016181229773462},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-01-18",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,18,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.7826518578292925,5.7826518578292925,null,null,4.7951778573158998,325,{"$f":"100*COUNT($AQ$31:AQ48)/$AQ$397","v":5.825242718446602},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-01-19",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,19,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.0046403367150196,5.0046403367150196,null,null,4.7248892723000004,108,{"$f":"100*COUNT($AQ$31:AQ49)/$AQ$397","v":6.1488673139158578},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-01-20",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,20,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.5307279661801969,5.5307279661801969,null,null,4.6883327738859997,249,{"$f":"100*COUNT($AQ$31:AQ50)/$AQ$397","v":6.4724919093851137},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-01-21",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,21,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,6.0935700733665419,6.0935700733665419,null,null,4.6863278128200001,10,{"$f":"100*COUNT($AQ$31:AQ51)/$AQ$397","v":6.7961165048543686},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-01-22",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,22,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.3205560432955714,5.3205560432955714,null,null,4.6353957378378849,86,{"$f":"100*COUNT($AQ$31:AQ52)/$AQ$397","v":7.1197411003236244},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-01-23",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,23,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.4129790640341184,5.4129790640341184,null,null,4.6353425624630997,364,{"$f":"100*COUNT($AQ$31:AQ53)/$AQ$397","v":7.4433656957928802},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-01-24",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,24,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.7142952468128012,5.7142952468128012,null,null,4.5848997434000003,69,{"$f":"100*COUNT($AQ$31:AQ54)/$AQ$397","v":7.766990291262136},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-01-25",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,25,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.6869635017765781,5.6869635017765781,null,null,4.5167615431422998,304,{"$f":"100*COUNT($AQ$31:AQ55)/$AQ$397","v":8.090614886731391},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-01-26",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,26,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.743770759389875,5.743770759389875,null,null,4.4873861743210997,122,{"$f":"100*COUNT($AQ$31:AQ56)/$AQ$397","v":8.4142394822006477},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-01-27",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,27,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.8259226138994045,5.8259226138994045,null,null,4.4873861743210997,223,{"$f":"100*COUNT($AQ$31:AQ57)/$AQ$397","v":8.7378640776699026},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-01-28",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,28,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,6.5868283363771098,6.5868283363771098,null,null,4.4786936781118998,247,{"$f":"100*COUNT($AQ$31:AQ58)/$AQ$397","v":9.0614886731391593},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-01-29",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,29,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.6260981413331894,5.6260981413331894,null,null,4.4567881698659999,315,{"$f":"100*COUNT($AQ$31:AQ59)/$AQ$397","v":9.3851132686084142},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-01-30",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,30,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.7168873869348786,5.7168873869348786,null,null,4.4522565752984997,230,{"$f":"100*COUNT($AQ$31:AQ60)/$AQ$397","v":9.7087378640776691},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-01-31",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,31,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.6022010029421745,5.6022010029421745,null,null,4.4172641587610002,9,{"$f":"100*COUNT($AQ$31:AQ61)/$AQ$397","v":10.032362459546926},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-02-01",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,32,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,8.2526122181299169,8.2526122181299169,null,null,4.3684825876842002,40,{"$f":"100*COUNT($AQ$31:AQ62)/$AQ$397","v":10.355987055016181},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-02-02",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,33,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,8.8045099770633843,8.8045099770633843,null,null,4.3646165646321551,27,{"$f":"100*COUNT($AQ$31:AQ63)/$AQ$397","v":10.679611650485437},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-02-03",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,34,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.8215859785130686,9.8215859785130686,null,null,4.3646165646321551,227,{"$f":"100*COUNT($AQ$31:AQ64)/$AQ$397","v":11.003236245954692},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-02-04",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,35,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,10.469162311177477,10.469162311177477,null,null,4.3499718787312336,302,{"$f":"100*COUNT($AQ$31:AQ65)/$AQ$397","v":11.326860841423947},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-02-05",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,36,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,7.1481369547919957,7.1481369547919957,null,null,4.3475239628100004,354,{"$f":"100*COUNT($AQ$31:AQ66)/$AQ$397","v":11.650485436893204},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-02-06",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,37,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,7.7261189434611337,7.7261189434611337,null,null,4.3475239628100004,70,{"$f":"100*COUNT($AQ$31:AQ67)/$AQ$397","v":11.974110032362459},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-02-07",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,38,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,8.1513954526847616,8.1513954526847616,null,null,4.2754695987259996,355,{"$f":"100*COUNT($AQ$31:AQ68)/$AQ$397","v":12.297734627831716},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-02-08",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,39,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.9328414342080666,5.9328414342080666,null,null,4.2691824643810001,270,{"$f":"100*COUNT($AQ$31:AQ69)/$AQ$397","v":12.621359223300971},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-02-09",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,40,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,6.6207633624461506,6.6207633624461506,null,null,4.2215878726350002,182,{"$f":"100*COUNT($AQ$31:AQ70)/$AQ$397","v":12.944983818770227},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-02-10",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,41,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.6119036572536807,9.6119036572536807,null,null,4.1671422894900001,159,{"$f":"100*COUNT($AQ$31:AQ71)/$AQ$397","v":13.268608414239482},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-02-11",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,42,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,8.6414557755735704,8.6414557755735704,null,null,4.1316324669847999,348,{"$f":"100*COUNT($AQ$31:AQ72)/$AQ$397","v":13.592233009708737},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-02-12",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,43,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,8.3406830919344337,8.3406830919344337,null,null,4.1293858122630001,58,{"$f":"100*COUNT($AQ$31:AQ73)/$AQ$397","v":13.915857605177994},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-02-13",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,44,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,7.7017734566646743,7.7017734566646743,null,null,4.1265973691519999,128,{"$f":"100*COUNT($AQ$31:AQ74)/$AQ$397","v":14.239482200647249},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-02-14",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,45,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.0027779923921649,9.0027779923921649,null,null,4.1233958787737999,240,{"$f":"100*COUNT($AQ$31:AQ75)/$AQ$397","v":14.563106796116505},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-02-15",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,46,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.8156077806788495,9.8156077806788495,null,null,3.9873298545495999,306,{"$f":"100*COUNT($AQ$31:AQ76)/$AQ$397","v":14.88673139158576},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-02-16",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,47,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.5872235902848928,9.5872235902848928,null,null,3.9787915254790001,264,{"$f":"100*COUNT($AQ$31:AQ77)/$AQ$397","v":15.210355987055015},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-02-17",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,48,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,10.712972161043931,10.712972161043931,null,null,3.9325421966178,139,{"$f":"100*COUNT($AQ$31:AQ78)/$AQ$397","v":15.533980582524272},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-02-18",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,49,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.4134272250492259,9.4134272250492259,null,null,3.9135489424848999,33,{"$f":"100*COUNT($AQ$31:AQ79)/$AQ$397","v":15.857605177993527},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-02-19",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,50,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.4767868562368758,5.4767868562368758,null,null,3.9113825927820001,178,{"$f":"100*COUNT($AQ$31:AQ80)/$AQ$397","v":16.181229773462782},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-02-20",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,51,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,7.3634354667173216,7.3634354667173216,null,null,3.8998495843810002,29,{"$f":"100*COUNT($AQ$31:AQ81)/$AQ$397","v":16.50485436893204},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-02-21",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,52,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,7.1060641977759964,7.1060641977759964,null,null,3.895147889955795,214,{"$f":"100*COUNT($AQ$31:AQ82)/$AQ$397","v":16.828478964401295},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-02-22",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,53,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,6.7744252906971374,6.7744252906971374,null,null,3.8872174973360001,51,{"$f":"100*COUNT($AQ$31:AQ83)/$AQ$397","v":17.15210355987055},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-02-23",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,54,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,7.4353531304490694,7.4353531304490694,null,null,3.8788183942500001,61,{"$f":"100*COUNT($AQ$31:AQ84)/$AQ$397","v":17.475728155339805},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-02-24",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,55,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.1953030656981731,9.1953030656981731,null,null,3.8467364554380001,4,{"$f":"100*COUNT($AQ$31:AQ85)/$AQ$397","v":17.79935275080906},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-02-25",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,56,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.6725829076566301,5.6725829076566301,null,null,3.8329672699800001,310,{"$f":"100*COUNT($AQ$31:AQ86)/$AQ$397","v":18.122977346278319},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-02-26",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,57,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.0358032431088624,5.0358032431088624,null,null,3.8274155699210999,166,{"$f":"100*COUNT($AQ$31:AQ87)/$AQ$397","v":18.446601941747574},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-02-27",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,58,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,8.6509139618561228,8.6509139618561228,null,null,3.782373278164,326,{"$f":"100*COUNT($AQ$31:AQ88)/$AQ$397","v":18.770226537216828},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-02-28",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,59,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,7.2043092670195392,7.2043092670195392,null,null,3.7688942331250002,250,{"$f":"100*COUNT($AQ$31:AQ89)/$AQ$397","v":19.093851132686083},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-03-01",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,60,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,10.348279700427366,10.348279700427366,null,null,3.7492792926772185,349,{"$f":"100*COUNT($AQ$31:AQ90)/$AQ$397","v":19.417475728155338},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-03-02",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,61,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,8.9566145722541712,8.9566145722541712,null,null,3.7366282673779998,234,{"$f":"100*COUNT($AQ$31:AQ91)/$AQ$397","v":19.741100323624597},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-03-03",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,62,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,10.156052727101965,10.156052727101965,null,null,3.7326568693829998,263,{"$f":"100*COUNT($AQ$31:AQ92)/$AQ$397","v":20.064724919093852},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-03-04",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,63,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,12.017409039357076,12.017409039357076,null,null,3.7244594674329998,340,{"$f":"100*COUNT($AQ$31:AQ93)/$AQ$397","v":20.388349514563107},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-03-05",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,64,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,8.5163619257995791,8.5163619257995791,null,null,3.7174584971451998,11,{"$f":"100*COUNT($AQ$31:AQ94)/$AQ$397","v":20.711974110032362},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-03-06",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,65,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,10.361621268819807,10.361621268819807,null,null,3.6942465843779999,174,{"$f":"100*COUNT($AQ$31:AQ95)/$AQ$397","v":21.035598705501616},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[{"$f":"A95+1","v":"2017-03-07"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"T95+1","v":66},{"$f":"IF(B96=\"\",,Seg1Vol*Seg1Fac/B96*C96)","v":0},{"$f":"Target*0.2828*D96^2.69*C96^0.15*0.933^(E96-5)","v":0},{"$f":"IF(V96=0,,U96/V96)","v":0},{"$f":"IF(B96=\"\",,Seg2Vol*Seg2Fac/B96*F96)","v":0},{"$f":"Target*0.2828*G96^2.69*F96^0.15*0.933^(H96-5)","v":0},{"$f":"IF(Y96=0,,X96/Y96)","v":0},{"$f":"IF(B96=\"\",,Seg3Vol*Seg3Fac/B96*I96)","v":0},{"$f":"Target*0.2828*J96^2.69*I96^0.15*0.933^(K96-5)","v":0},{"$f":"IF(AB96=0,,AA96/AB96)","v":0},{"$f":"IF(B96=\"\",,Seg4Vol*Seg4Fac/B96*L96)","v":0},{"$f":"Target*0.2828*M96^2.69*L96^0.15*0.933^(N96-5)","v":0},{"$f":"IF(AE96=0,,AD96/AE96)","v":0},{"$f":"IF(B96=\"\",,Seg5Vol*O96*Seg5Fac/B96*P96)","v":0},{"$f":"Target*0.2828*Q96^2.69*P96^0.15*0.933^(R96-5)","v":0},{"$f":"IF(AH96=0,,AG96/AH96)","v":0},{"$f":"W96+Z96+AC96+AF96+AI96","v":0},{"$f":"AJ96*Target","v":0},null,6.7734621782225375,6.7734621782225375,null,null,3.6866479322360002,5,{"$f":"100*COUNT($AQ$31:AQ96)/$AQ$397","v":21.359223300970875},null,{"$f":"$AU$29","v":0},{"$f":"+$AV$29","v":0},null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-03-08",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,67,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,11.107829918178886,11.107829918178886,null,null,3.6811143367752002,309,{"$f":"100*COUNT($AQ$31:AQ97)/$AQ$397","v":21.68284789644013},null,0,0,null,{"$f":"$AX$29","v":{"$error":"#DIV/0!"}},{"$f":"+$AY$29","v":{"$error":"#DIV/0!"}}]
["2017-03-09",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,68,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,11.006005418332469,11.006005418332469,null,null,3.6623994815221002,279,{"$f":"100*COUNT($AQ$31:AQ98)/$AQ$397","v":22.006472491909385},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-03-10",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,69,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,10.553476645070244,10.553476645070244,null,null,3.6464629966254001,172,{"$f":"100*COUNT($AQ$31:AQ99)/$AQ$397","v":22.33009708737864},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-03-11",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,70,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.7951094209621559,9.7951094209621559,null,null,3.6412435399546004,189,{"$f":"100*COUNT($AQ$31:AQ100)/$AQ$397","v":22.653721682847895},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-03-12",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,71,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.4257977385924576,9.4257977385924576,null,null,3.5964727954817,198,{"$f":"100*COUNT($AQ$31:AQ101)/$AQ$397","v":22.977346278317153},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-03-13",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,72,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,8.5708077916724008,8.5708077916724008,null,null,3.5852378161909999,321,{"$f":"100*COUNT($AQ$31:AQ102)/$AQ$397","v":23.300970873786408},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-03-14",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,73,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,7.0578551095286821,7.0578551095286821,null,null,3.5831757173257404,131,{"$f":"100*COUNT($AQ$31:AQ103)/$AQ$397","v":23.624595469255663},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-03-15",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,74,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.712204366141993,9.712204366141993,null,null,3.5797345397870002,3,{"$f":"100*COUNT($AQ$31:AQ104)/$AQ$397","v":23.948220064724918},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-03-16",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,75,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.0368547888661421,9.0368547888661421,null,null,3.5747166875462648,8,{"$f":"100*COUNT($AQ$31:AQ105)/$AQ$397","v":24.271844660194176},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-03-17",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,76,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.7307207598736625,9.7307207598736625,null,null,3.5721689897351081,288,{"$f":"100*COUNT($AQ$31:AQ106)/$AQ$397","v":24.595469255663431},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-03-18",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,77,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,8.5782138607527827,8.5782138607527827,null,null,3.5445756316743844,142,{"$f":"100*COUNT($AQ$31:AQ107)/$AQ$397","v":24.919093851132686},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-03-19",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,78,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,10.690496590749158,10.690496590749158,null,null,3.521111564521,77,{"$f":"100*COUNT($AQ$31:AQ108)/$AQ$397","v":25.242718446601941},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-03-20",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,79,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,8.4058912335007445,8.4058912335007445,null,null,3.5119539745836175,149,{"$f":"100*COUNT($AQ$31:AQ109)/$AQ$397","v":25.566343042071196},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-03-21",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,80,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,7.5971575099643065,7.5971575099643065,null,null,3.4974284523299999,144,{"$f":"100*COUNT($AQ$31:AQ110)/$AQ$397","v":25.889967637540455},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-03-22",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,81,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.2414008895930486,9.2414008895930486,null,null,3.4939679665449002,320,{"$f":"100*COUNT($AQ$31:AQ111)/$AQ$397","v":26.21359223300971},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-03-23",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,82,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.1011613666755089,9.1011613666755089,null,null,3.4691872256291001,12,{"$f":"100*COUNT($AQ$31:AQ112)/$AQ$397","v":26.537216828478964},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-03-24",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,83,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,13.925095635786031,13.925095635786031,null,null,3.4683338134850001,238,{"$f":"100*COUNT($AQ$31:AQ113)/$AQ$397","v":26.860841423948219},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-03-25",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,84,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,11.099811208177979,11.099811208177979,null,null,3.4577614732782109,52,{"$f":"100*COUNT($AQ$31:AQ114)/$AQ$397","v":27.184466019417474},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-03-26",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,85,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,11.017050939100377,11.017050939100377,null,null,3.4535923825447998,248,{"$f":"100*COUNT($AQ$31:AQ115)/$AQ$397","v":27.508090614886733},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-03-27",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,86,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,10.046033087002959,10.046033087002959,null,null,3.4535923825447998,215,{"$f":"100*COUNT($AQ$31:AQ116)/$AQ$397","v":27.831715210355988},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-03-28",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,87,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,11.133747972317799,11.133747972317799,null,null,3.4485531353000001,164,{"$f":"100*COUNT($AQ$31:AQ117)/$AQ$397","v":28.155339805825243},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-03-29",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,88,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.8010851141037758,9.8010851141037758,null,null,3.4458728592286998,311,{"$f":"100*COUNT($AQ$31:AQ118)/$AQ$397","v":28.478964401294498},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-03-30",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,89,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,12.508065842109206,12.508065842109206,null,null,3.4443335398611237,45,{"$f":"100*COUNT($AQ$31:AQ119)/$AQ$397","v":28.802588996763753},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-03-31",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,90,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,12.689235622151319,12.689235622151319,null,null,3.4423666431352,71,{"$f":"100*COUNT($AQ$31:AQ120)/$AQ$397","v":29.126213592233011},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-01",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,91,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,10.195476963922431,10.195476963922431,null,null,3.4223294375669999,105,{"$f":"100*COUNT($AQ$31:AQ121)/$AQ$397","v":29.449838187702266},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-02",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,92,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,10.912484997019872,10.912484997019872,null,null,3.4211973691732438,317,{"$f":"100*COUNT($AQ$31:AQ122)/$AQ$397","v":29.773462783171521},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-03",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,93,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.6765127103738102,9.6765127103738102,null,null,3.4126326879672,190,{"$f":"100*COUNT($AQ$31:AQ123)/$AQ$397","v":30.097087378640776},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-04",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,94,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.698165452270608,9.698165452270608,null,null,3.3863392215590999,197,{"$f":"100*COUNT($AQ$31:AQ124)/$AQ$397","v":30.420711974110031},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-05",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,95,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,10.1227509980435,10.1227509980435,null,null,3.3412363966554999,258,{"$f":"100*COUNT($AQ$31:AQ125)/$AQ$397","v":30.744336569579289},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-06",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,96,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,13.430971343589967,13.430971343589967,null,null,3.3411693196821313,204,{"$f":"100*COUNT($AQ$31:AQ126)/$AQ$397","v":31.067961165048544},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-07",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,97,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.6830341939433069,9.6830341939433069,null,null,3.3214444491819002,123,{"$f":"100*COUNT($AQ$31:AQ127)/$AQ$397","v":31.391585760517799},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-08",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,98,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,10.481463141884802,10.481463141884802,null,null,3.3156153243320001,59,{"$f":"100*COUNT($AQ$31:AQ128)/$AQ$397","v":31.715210355987054},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-09",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,99,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,11.000913269919135,11.000913269919135,null,null,3.2977661551861814,256,{"$f":"100*COUNT($AQ$31:AQ129)/$AQ$397","v":32.038834951456309},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-10",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,100,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,12.600348435241477,12.600348435241477,null,null,3.289946812193,146,{"$f":"100*COUNT($AQ$31:AQ130)/$AQ$397","v":32.362459546925564},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-11",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,101,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,10.378963401964276,10.378963401964276,null,null,3.2749752462920001,342,{"$f":"100*COUNT($AQ$31:AQ131)/$AQ$397","v":32.686084142394819},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-12",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,102,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,14.353712580224972,14.353712580224972,null,null,3.2715165611764037,103,{"$f":"100*COUNT($AQ$31:AQ132)/$AQ$397","v":33.009708737864081},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-13",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,103,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,8.6172910087134511,8.6172910087134511,null,null,3.2458845673800001,192,{"$f":"100*COUNT($AQ$31:AQ133)/$AQ$397","v":33.333333333333336},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-14",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,104,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,10.443841593171543,10.443841593171543,null,null,3.1958732859889998,356,{"$f":"100*COUNT($AQ$31:AQ134)/$AQ$397","v":33.656957928802591},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-15",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,105,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,11.658892068286022,11.658892068286022,null,null,3.1884739671529614,218,{"$f":"100*COUNT($AQ$31:AQ135)/$AQ$397","v":33.980582524271846},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-16",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,106,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,8.9418321986480365,8.9418321986480365,null,null,3.1884739671529614,57,{"$f":"100*COUNT($AQ$31:AQ136)/$AQ$397","v":34.3042071197411},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-17",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,107,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.7670123438635521,9.7670123438635521,null,null,3.1875363867274,212,{"$f":"100*COUNT($AQ$31:AQ137)/$AQ$397","v":34.627831715210355},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-18",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,108,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.6654596313537127,9.6654596313537127,null,null,3.185114542689,285,{"$f":"100*COUNT($AQ$31:AQ138)/$AQ$397","v":34.95145631067961},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-19",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,109,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,10.953193783708073,10.953193783708073,null,null,3.185114542689,148,{"$f":"100*COUNT($AQ$31:AQ139)/$AQ$397","v":35.275080906148865},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-20",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,110,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,12.304054500020122,12.304054500020122,null,null,3.185114542689,177,{"$f":"100*COUNT($AQ$31:AQ140)/$AQ$397","v":35.59870550161812},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-21",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,111,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,15.569024086377407,15.569024086377407,null,null,3.1568964797999999,65,{"$f":"100*COUNT($AQ$31:AQ141)/$AQ$397","v":35.922330097087375},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-22",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,112,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,13.921696333479989,13.921696333479989,null,null,3.137874738468148,333,{"$f":"100*COUNT($AQ$31:AQ142)/$AQ$397","v":36.245954692556637},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-23",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,113,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,13.305415206463135,13.305415206463135,null,null,3.1373677839125924,60,{"$f":"100*COUNT($AQ$31:AQ143)/$AQ$397","v":36.569579288025892},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-24",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,114,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,10.376067256222141,10.376067256222141,null,null,3.1365211472699999,82,{"$f":"100*COUNT($AQ$31:AQ144)/$AQ$397","v":36.893203883495147},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-25",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,115,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,11.5931866159425,11.5931866159425,null,null,3.117572521384,206,{"$f":"100*COUNT($AQ$31:AQ145)/$AQ$397","v":37.216828478964402},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-26",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,116,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,10.18997385339398,10.18997385339398,null,null,2.9449315441961001,83,{"$f":"100*COUNT($AQ$31:AQ146)/$AQ$397","v":37.540453074433657},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-27",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,117,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,12.429353738469395,12.429353738469395,null,null,2.938223628891,284,{"$f":"100*COUNT($AQ$31:AQ147)/$AQ$397","v":37.864077669902912},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-28",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,118,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,13.302983235188847,13.302983235188847,null,null,2.8888333637430001,327,{"$f":"100*COUNT($AQ$31:AQ148)/$AQ$397","v":38.187702265372167},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-29",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,119,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.8851816101973338,9.8851816101973338,null,null,2.8717474617579999,134,{"$f":"100*COUNT($AQ$31:AQ149)/$AQ$397","v":38.511326860841422},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-04-30",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,120,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.1529845287520377,9.1529845287520377,null,null,2.8688822766138999,316,{"$f":"100*COUNT($AQ$31:AQ150)/$AQ$397","v":38.834951456310677},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-05-01",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,121,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,10.230686477259443,10.230686477259443,null,null,2.8447882842790002,141,{"$f":"100*COUNT($AQ$31:AQ151)/$AQ$397","v":39.158576051779939},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-05-02",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,122,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,12.584405073744952,12.584405073744952,null,null,2.8434431722836,100,{"$f":"100*COUNT($AQ$31:AQ152)/$AQ$397","v":39.482200647249194},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-05-03",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,123,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,17.47899065385079,17.47899065385079,null,null,2.8164266482864537,56,{"$f":"100*COUNT($AQ$31:AQ153)/$AQ$397","v":39.805825242718448},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-05-04",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,124,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,15.419289855008568,15.419289855008568,null,null,2.7988317448719999,194,{"$f":"100*COUNT($AQ$31:AQ154)/$AQ$397","v":40.129449838187703},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-05-05",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,125,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,15.537366316930418,15.537366316930418,null,null,2.7939592437399998,183,{"$f":"100*COUNT($AQ$31:AQ155)/$AQ$397","v":40.453074433656958},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-05-06",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,126,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,13.078514005475792,13.078514005475792,null,null,2.7785875746256998,26,{"$f":"100*COUNT($AQ$31:AQ156)/$AQ$397","v":40.776699029126213},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-05-07",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,127,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,12.952941319041468,12.952941319041468,null,null,2.7744692281825225,161,{"$f":"100*COUNT($AQ$31:AQ157)/$AQ$397","v":41.100323624595468},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-05-08",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,128,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,13.831527970297813,13.831527970297813,null,null,2.7463454593418,193,{"$f":"100*COUNT($AQ$31:AQ158)/$AQ$397","v":41.423948220064723},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-05-09",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,129,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,14.648413184900788,14.648413184900788,null,null,2.7376265326599998,357,{"$f":"100*COUNT($AQ$31:AQ159)/$AQ$397","v":41.747572815533978},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[{"$f":"A159+1","v":"2017-05-10"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"T159+1","v":130},{"$f":"IF(B160=\"\",,Seg1Vol*Seg1Fac/B160*C160)","v":0},{"$f":"Target*0.2828*D160^2.69*C160^0.15*0.933^(E160-5)","v":0},{"$f":"IF(V160=0,,U160/V160)","v":0},{"$f":"IF(B160=\"\",,Seg2Vol*Seg2Fac/B160*F160)","v":0},{"$f":"Target*0.2828*G160^2.69*F160^0.15*0.933^(H160-5)","v":0},{"$f":"IF(Y160=0,,X160/Y160)","v":0},{"$f":"IF(B160=\"\",,Seg3Vol*Seg3Fac/B160*I160)","v":0},{"$f":"Target*0.2828*J160^2.69*I160^0.15*0.933^(K160-5)","v":0},{"$f":"IF(AB160=0,,AA160/AB160)","v":0},{"$f":"IF(B160=\"\",,Seg4Vol*Seg4Fac/B160*L160)","v":0},{"$f":"Target*0.2828*M160^2.69*L160^0.15*0.933^(N160-5)","v":0},{"$f":"IF(AE160=0,,AD160/AE160)","v":0},{"$f":"IF(B160=\"\",,Seg5Vol*O160*Seg5Fac/B160*P160)","v":0},{"$f":"Target*0.2828*Q160^2.69*P160^0.15*0.933^(R160-5)","v":0},{"$f":"IF(AH160=0,,AG160/AH160)","v":0},{"$f":"W160+Z160+AC160+AF160+AI160","v":0},{"$f":"AJ160*Target","v":0},null,12.528390570265168,12.528390570265168,null,null,2.7366265417140001,109,{"$f":"100*COUNT($AQ$31:AQ160)/$AQ$397","v":42.071197411003233},null,{"$f":"$AU$29","v":0},{"$f":"+$AV$29","v":0},null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-05-11",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,131,0,0,0,0,0,0,{"$f":"IF(B161=\"\",,Seg3Vol*Seg3Fac/B161*I161)","v":0},{"$f":"Target*0.2828*J161^2.69*I161^0.15*0.933^(K161-5)","v":0},{"$f":"IF(AB161=0,,AA161/AB161)","v":0},0,0,0,0,0,0,0,0,null,14.63136375271073,14.63136375271073,null,null,2.6838912256867369,145,{"$f":"100*COUNT($AQ$31:AQ161)/$AQ$397","v":42.394822006472495},null,0,0,null,{"$f":"$AX$29","v":{"$error":"#DIV/0!"}},{"$f":"+$AY$29","v":{"$error":"#DIV/0!"}}]
["2017-05-12",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,132,0,0,0,0,0,0,{"$f":"IF(B162=\"\",,Seg3Vol*Seg3Fac/B162*I162)","v":0},{"$f":"Target*0.2828*J162^2.69*I162^0.15*0.933^(K162-5)","v":0},{"$f":"IF(AB162=0,,AA162/AB162)","v":0},0,0,0,0,0,0,0,0,null,25.004872554680396,25.004872554680396,null,null,2.6645987946997001,67,{"$f":"100*COUNT($AQ$31:AQ162)/$AQ$397","v":42.71844660194175},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-05-13",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,133,0,0,0,0,0,0,{"$f":"IF(B163=\"\",,Seg3Vol*Seg3Fac/B163*I163)","v":0},{"$f":"Target*0.2828*J163^2.69*I163^0.15*0.933^(K163-5)","v":0},{"$f":"IF(AB163=0,,AA163/AB163)","v":0},0,0,0,0,0,0,0,0,null,15.323318189268047,15.323318189268047,null,null,2.6629739953459999,90,{"$f":"100*COUNT($AQ$31:AQ163)/$AQ$397","v":43.042071197411005},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-05-14",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,134,0,0,0,0,0,0,{"$f":"IF(B164=\"\",,Seg3Vol*Seg3Fac/B164*I164)","v":0},{"$f":"Target*0.2828*J164^2.69*I164^0.15*0.933^(K164-5)","v":0},{"$f":"IF(AB164=0,,AA164/AB164)","v":0},0,0,0,0,0,0,0,0,null,14.985149071415705,14.985149071415705,null,null,2.657783891317,18,{"$f":"100*COUNT($AQ$31:AQ164)/$AQ$397","v":43.36569579288026},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-05-15",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,135,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,17.332041769371955,17.332041769371955,null,null,2.6268647144899999,39,{"$f":"100*COUNT($AQ$31:AQ165)/$AQ$397","v":43.689320388349515},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-05-16",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,136,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,20.571468001115505,20.571468001115505,null,null,2.6268647144899999,209,{"$f":"100*COUNT($AQ$31:AQ166)/$AQ$397","v":44.01294498381877},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-05-17",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,137,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,22.085346381013959,22.085346381013959,null,null,2.5961739939965001,163,{"$f":"100*COUNT($AQ$31:AQ167)/$AQ$397","v":44.336569579288025},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-05-18",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,138,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,19.237126640561982,19.237126640561982,null,null,2.5955239296700001,253,{"$f":"100*COUNT($AQ$31:AQ168)/$AQ$397","v":44.660194174757279},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-05-19",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,139,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,24.679844935362489,24.679844935362489,null,null,2.5921885651486001,210,{"$f":"100*COUNT($AQ$31:AQ169)/$AQ$397","v":44.983818770226534},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-05-20",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,140,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,15.544633543694014,15.544633543694014,null,null,2.5556673481210002,312,{"$f":"100*COUNT($AQ$31:AQ170)/$AQ$397","v":45.307443365695789},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-05-21",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,141,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,20.613206501338695,20.613206501338695,null,null,2.5196963491378002,332,{"$f":"100*COUNT($AQ$31:AQ171)/$AQ$397","v":45.631067961165051},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-05-22",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,142,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,18.0218044256073,18.0218044256073,null,null,2.3946163614921634,324,{"$f":"100*COUNT($AQ$31:AQ172)/$AQ$397","v":45.954692556634306},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-05-23",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,143,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,15.973755641764328,15.973755641764328,null,null,2.3841243399732646,92,{"$f":"100*COUNT($AQ$31:AQ173)/$AQ$397","v":46.278317152103561},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-05-24",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,144,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,17.276194416458345,17.276194416458345,null,null,2.3555511675613001,44,{"$f":"100*COUNT($AQ$31:AQ174)/$AQ$397","v":46.601941747572816},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-05-25",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,145,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,20.020712630156943,20.020712630156943,null,null,2.323597529737,133,{"$f":"100*COUNT($AQ$31:AQ175)/$AQ$397","v":46.925566343042071},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-05-26",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,146,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,16.55940971664549,16.55940971664549,null,null,2.3138725191942,127,{"$f":"100*COUNT($AQ$31:AQ176)/$AQ$397","v":47.249190938511326},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-05-27",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,147,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,18.625340084581598,18.625340084581598,null,null,2.3132595767652,104,{"$f":"100*COUNT($AQ$31:AQ177)/$AQ$397","v":47.572815533980581},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-05-28",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,148,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,20.954057706091085,20.954057706091085,null,null,2.2941332839949,322,{"$f":"100*COUNT($AQ$31:AQ178)/$AQ$397","v":47.896440129449836},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-05-29",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,149,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,18.921096374951773,18.921096374951773,null,null,2.289329586,179,{"$f":"100*COUNT($AQ$31:AQ179)/$AQ$397","v":48.220064724919091},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-05-30",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,150,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,18.709233015457286,18.709233015457286,null,null,2.2628469235579001,254,{"$f":"100*COUNT($AQ$31:AQ180)/$AQ$397","v":48.543689320388353},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-05-31",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,151,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,19.676741125809254,19.676741125809254,null,null,2.2441334619990001,85,{"$f":"100*COUNT($AQ$31:AQ181)/$AQ$397","v":48.867313915857608},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-01",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,152,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,20.091853880317991,20.091853880317991,null,null,2.2438881372784896,73,{"$f":"100*COUNT($AQ$31:AQ182)/$AQ$397","v":49.190938511326863},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-02",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,153,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,17.740662718161211,17.740662718161211,null,null,2.2386276587579998,72,{"$f":"100*COUNT($AQ$31:AQ183)/$AQ$397","v":49.514563106796118},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-03",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,154,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,16.593249561363031,16.593249561363031,null,null,2.2384644425000002,236,{"$f":"100*COUNT($AQ$31:AQ184)/$AQ$397","v":49.838187702265373},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-04",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,155,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,21.922031599313982,21.922031599313982,null,null,2.2299551626329999,267,{"$f":"100*COUNT($AQ$31:AQ185)/$AQ$397","v":50.161812297734627},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-05",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,156,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,20.183362575302024,20.183362575302024,null,null,2.2261317646836001,244,{"$f":"100*COUNT($AQ$31:AQ186)/$AQ$397","v":50.485436893203882},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-06",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,157,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,19.399410354956338,19.399410354956338,null,null,2.1919662115717999,195,{"$f":"100*COUNT($AQ$31:AQ187)/$AQ$397","v":50.809061488673137},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-07",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,158,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,17.993556855856763,17.993556855856763,null,null,2.1782191691600001,137,{"$f":"100*COUNT($AQ$31:AQ188)/$AQ$397","v":51.132686084142392},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-08",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,159,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,23.205857523255528,23.205857523255528,null,null,2.1534211669469001,237,{"$f":"100*COUNT($AQ$31:AQ189)/$AQ$397","v":51.456310679611647},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-09",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,160,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,16.469539812353315,16.469539812353315,null,null,2.13725432758,277,{"$f":"100*COUNT($AQ$31:AQ190)/$AQ$397","v":51.779935275080909},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-10",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,161,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,21.120696142513815,21.120696142513815,null,null,2.1345773922800002,307,{"$f":"100*COUNT($AQ$31:AQ191)/$AQ$397","v":52.103559870550164},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-11",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,162,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,21.459938611675771,21.459938611675771,null,null,2.128392865576,202,{"$f":"100*COUNT($AQ$31:AQ192)/$AQ$397","v":52.427184466019419},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-12",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,163,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,23.164374704668148,23.164374704668148,null,null,2.1224556957630001,150,{"$f":"100*COUNT($AQ$31:AQ193)/$AQ$397","v":52.750809061488674},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-13",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,164,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,21.247918324035268,21.247918324035268,null,null,2.1175419986000001,168,{"$f":"100*COUNT($AQ$31:AQ194)/$AQ$397","v":53.074433656957929},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-14",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,165,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,28.457270488285879,28.457270488285879,null,null,1.9934955964858294,151,{"$f":"100*COUNT($AQ$31:AQ195)/$AQ$397","v":53.398058252427184},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-15",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,166,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,23.077829222662373,23.077829222662373,null,null,1.9812592783,245,{"$f":"100*COUNT($AQ$31:AQ196)/$AQ$397","v":53.721682847896439},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-16",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,167,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,28.528053162281555,28.528053162281555,null,null,1.9789141356993361,350,{"$f":"100*COUNT($AQ$31:AQ197)/$AQ$397","v":54.045307443365694},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-17",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,168,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,35.619329492117643,35.619329492117643,null,null,1.976258417131,235,{"$f":"100*COUNT($AQ$31:AQ198)/$AQ$397","v":54.368932038834949},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-18",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,169,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,28.758159033048361,28.758159033048361,null,null,1.9697691611299999,305,{"$f":"100*COUNT($AQ$31:AQ199)/$AQ$397","v":54.692556634304211},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-19",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,170,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,20.091106748301414,20.091106748301414,null,null,1.9673796535217001,78,{"$f":"100*COUNT($AQ$31:AQ200)/$AQ$397","v":55.016181229773466},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-20",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,171,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,31.723847467729836,31.723847467729836,null,null,1.9651533373336838,303,{"$f":"100*COUNT($AQ$31:AQ201)/$AQ$397","v":55.339805825242721},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-21",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,172,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,30.162629097894129,30.162629097894129,null,null,1.9624985881100001,299,{"$f":"100*COUNT($AQ$31:AQ202)/$AQ$397","v":55.663430420711975},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-22",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,173,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,31.439833998349823,31.439833998349823,null,null,1.9569329983499999,335,{"$f":"100*COUNT($AQ$31:AQ203)/$AQ$397","v":55.98705501618123},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-23",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,174,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,26.646706216577368,26.646706216577368,null,null,1.9493689983646001,231,{"$f":"100*COUNT($AQ$31:AQ204)/$AQ$397","v":56.310679611650485},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-24",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,175,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,44.263525540285755,44.263525540285755,null,null,1.9457988977426,118,{"$f":"100*COUNT($AQ$31:AQ205)/$AQ$397","v":56.63430420711974},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-25",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,176,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,31.7897365256567,31.7897365256567,null,null,1.9433395626768999,273,{"$f":"100*COUNT($AQ$31:AQ206)/$AQ$397","v":56.957928802588995},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-26",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,177,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,34.011030340854184,34.011030340854184,null,null,1.93346619422,75,{"$f":"100*COUNT($AQ$31:AQ207)/$AQ$397","v":57.28155339805825},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-27",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,178,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,33.751151522581125,33.751151522581125,null,null,1.9248671397319808,115,{"$f":"100*COUNT($AQ$31:AQ208)/$AQ$397","v":57.605177993527505},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-28",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,179,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,33.432641003440303,33.432641003440303,null,null,1.91623441118,120,{"$f":"100*COUNT($AQ$31:AQ209)/$AQ$397","v":57.928802588996767},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-29",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,180,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,31.475685648031082,31.475685648031082,null,null,1.9127921281575999,23,{"$f":"100*COUNT($AQ$31:AQ210)/$AQ$397","v":58.252427184466022},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-06-30",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,181,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,37.920402551681498,37.920402551681498,null,null,1.9116824355569999,117,{"$f":"100*COUNT($AQ$31:AQ211)/$AQ$397","v":58.576051779935277},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-07-01",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,182,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,20.253583764625553,20.253583764625553,null,null,1.8993198777442657,239,{"$f":"100*COUNT($AQ$31:AQ212)/$AQ$397","v":58.899676375404532},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-07-02",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,183,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,23.886304135455685,23.886304135455685,null,null,1.8949715954962001,35,{"$f":"100*COUNT($AQ$31:AQ213)/$AQ$397","v":59.223300970873787},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-07-03",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,184,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,34.224709778055612,34.224709778055612,null,null,1.8946823491577001,1,{"$f":"100*COUNT($AQ$31:AQ214)/$AQ$397","v":59.546925566343042},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-07-04",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,185,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,34.113264806528001,34.113264806528001,null,null,1.8919463148146001,243,{"$f":"100*COUNT($AQ$31:AQ215)/$AQ$397","v":59.870550161812297},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-07-05",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,186,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,33.387662859629934,33.387662859629934,null,null,1.8868692721396001,185,{"$f":"100*COUNT($AQ$31:AQ216)/$AQ$397","v":60.194174757281552},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-07-06",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,187,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,29.151807086165835,29.151807086165835,null,null,1.879873454962,242,{"$f":"100*COUNT($AQ$31:AQ217)/$AQ$397","v":60.517799352750806},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-07-07",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,188,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,25.830595801541882,25.830595801541882,null,null,1.8749248911281,21,{"$f":"100*COUNT($AQ$31:AQ218)/$AQ$397","v":60.841423948220061},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-07-08",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,189,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,28.497176484117439,28.497176484117439,null,null,1.8687592541319999,158,{"$f":"100*COUNT($AQ$31:AQ219)/$AQ$397","v":61.165048543689323},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-07-09",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,190,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,31.836923419564602,31.836923419564602,null,null,1.8679783137448149,16,{"$f":"100*COUNT($AQ$31:AQ220)/$AQ$397","v":61.488673139158578},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-07-10",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,191,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,29.740919633930826,29.740919633930826,null,null,1.863913919779469,275,{"$f":"100*COUNT($AQ$31:AQ221)/$AQ$397","v":61.812297734627833},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-07-11",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,192,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,40.702110566583038,40.702110566583038,null,null,1.8589648399350001,140,{"$f":"100*COUNT($AQ$31:AQ222)/$AQ$397","v":62.135922330097088},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-07-12",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,193,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,30.903294877381715,30.903294877381715,null,null,1.8556868547200001,199,{"$f":"100*COUNT($AQ$31:AQ223)/$AQ$397","v":62.459546925566343},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[{"$f":"A223+1","v":"2017-07-13"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"T223+1","v":194},{"$f":"IF(B224=\"\",,Seg1Vol*Seg1Fac/B224*C224)","v":0},{"$f":"Target*0.2828*D224^2.69*C224^0.15*0.933^(E224-5)","v":0},{"$f":"IF(V224=0,,U224/V224)","v":0},{"$f":"IF(B224=\"\",,Seg2Vol*Seg2Fac/B224*F224)","v":0},{"$f":"Target*0.2828*G224^2.69*F224^0.15*0.933^(H224-5)","v":0},{"$f":"IF(Y224=0,,X224/Y224)","v":0},0,0,0,{"$f":"IF(B224=\"\",,Seg4Vol*Seg4Fac/B224*L224)","v":0},{"$f":"Target*0.2828*M224^2.69*L224^0.15*0.933^(N224-5)","v":0},{"$f":"IF(AE224=0,,AD224/AE224)","v":0},{"$f":"IF(B224=\"\",,Seg5Vol*O224*Seg5Fac/B224*P224)","v":0},{"$f":"Target*0.2828*Q224^2.69*P224^0.15*0.933^(R224-5)","v":0},{"$f":"IF(AH224=0,,AG224/AH224)","v":0},{"$f":"W224+Z224+AC224+AF224+AI224","v":0},{"$f":"AJ224*Target","v":0},null,36.952274798297374,36.952274798297374,null,null,1.8545159714668999,352,{"$f":"100*COUNT($AQ$31:AQ224)/$AQ$397","v":62.783171521035598},null,{"$f":"$AU$29","v":0},{"$f":"+$AV$29","v":0},null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-07-14",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,195,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,37.959631887110227,37.959631887110227,null,null,1.8545159714668999,24,{"$f":"100*COUNT($AQ$31:AQ225)/$AQ$397","v":63.106796116504853},null,0,0,null,{"$f":"$AX$29","v":{"$error":"#DIV/0!"}},{"$f":"+$AY$29","v":{"$error":"#DIV/0!"}}]
["2017-07-15",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,196,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,37.189845108289013,37.189845108289013,null,null,1.8545159714668999,155,{"$f":"100*COUNT($AQ$31:AQ226)/$AQ$397","v":63.430420711974108},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-07-16",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,197,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,33.219140258974036,33.219140258974036,null,null,1.8545159714668999,203,{"$f":"100*COUNT($AQ$31:AQ227)/$AQ$397","v":63.754045307443363},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-07-17",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,198,0,0,0,0,0,0,{"$f":"IF(B228=\"\",,Seg3Vol*Seg3Fac/B228*I228)","v":0},{"$f":"Target*0.2828*J228^2.69*I228^0.15*0.933^(K228-5)","v":0},{"$f":"IF(AB228=0,,AA228/AB228)","v":0},0,0,0,0,0,0,0,0,null,34.724569228732527,34.724569228732527,null,null,1.8258117782579999,297,{"$f":"100*COUNT($AQ$31:AQ228)/$AQ$397","v":64.077669902912618},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-07-18",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,199,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,24.154724026850971,24.154724026850971,null,null,1.8249985918116098,15,{"$f":"100*COUNT($AQ$31:AQ229)/$AQ$397","v":64.401294498381873},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-07-19",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,200,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,32.636393592554874,32.636393592554874,null,null,1.8249945954586999,171,{"$f":"100*COUNT($AQ$31:AQ230)/$AQ$397","v":64.724919093851128},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-07-20",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,201,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,31.270195183685722,31.270195183685722,null,null,1.821649681166714,63,{"$f":"100*COUNT($AQ$31:AQ231)/$AQ$397","v":65.048543689320383},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-07-21",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,202,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,37.273588149408731,37.273588149408731,null,null,1.8144366629312438,173,{"$f":"100*COUNT($AQ$31:AQ232)/$AQ$397","v":65.372168284789637},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-07-22",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,203,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,34.734107463509837,34.734107463509837,null,null,1.7974895477899999,76,{"$f":"100*COUNT($AQ$31:AQ233)/$AQ$397","v":65.695792880258907},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-07-23",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,204,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,34.204078277155318,34.204078277155318,null,null,1.7861116442145104,157,{"$f":"100*COUNT($AQ$31:AQ234)/$AQ$397","v":66.019417475728162},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-07-24",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,205,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,32.586688971829346,32.586688971829346,null,null,1.7833261261291,79,{"$f":"100*COUNT($AQ$31:AQ235)/$AQ$397","v":66.343042071197416},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-07-25",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,206,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,30.576036076123046,30.576036076123046,null,null,1.782676994114631,281,{"$f":"100*COUNT($AQ$31:AQ236)/$AQ$397","v":66.666666666666671},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-07-26",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,207,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,33.206841890638664,33.206841890638664,null,null,1.781291462585,49,{"$f":"100*COUNT($AQ$31:AQ237)/$AQ$397","v":66.990291262135926},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-07-27",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,208,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,30.425720387637746,30.425720387637746,null,null,1.781291462585,252,{"$f":"100*COUNT($AQ$31:AQ238)/$AQ$397","v":67.313915857605181},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-07-28",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,209,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,29.086231734059957,29.086231734059957,null,null,1.7797541998829001,66,{"$f":"100*COUNT($AQ$31:AQ239)/$AQ$397","v":67.637540453074436},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-07-29",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,210,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,26.681852686962898,26.681852686962898,null,null,1.7784826641718674,257,{"$f":"100*COUNT($AQ$31:AQ240)/$AQ$397","v":67.961165048543691},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-07-30",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,211,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,30.316197094477157,30.316197094477157,null,null,1.7721915656356999,152,{"$f":"100*COUNT($AQ$31:AQ241)/$AQ$397","v":68.284789644012946},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-07-31",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,212,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,26.115685733075487,26.115685733075487,null,null,1.767116659961,339,{"$f":"100*COUNT($AQ$31:AQ242)/$AQ$397","v":68.608414239482201},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-01",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,213,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,12.974211921333428,12.974211921333428,null,null,1.7598294452709999,46,{"$f":"100*COUNT($AQ$31:AQ243)/$AQ$397","v":68.932038834951456},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-02",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,214,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,28.159859200876731,28.159859200876731,null,null,1.757172536176,36,{"$f":"100*COUNT($AQ$31:AQ244)/$AQ$397","v":69.255663430420711},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-03",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,215,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,36.399444590167349,36.399444590167349,null,null,1.7534437684963,13,{"$f":"100*COUNT($AQ$31:AQ245)/$AQ$397","v":69.579288025889966},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-04",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,216,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,46.163748528481143,46.163748528481143,null,null,1.7497863735537122,351,{"$f":"100*COUNT($AQ$31:AQ246)/$AQ$397","v":69.902912621359221},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-05",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,217,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,39.579551183830297,39.579551183830297,null,null,1.7456233686136,286,{"$f":"100*COUNT($AQ$31:AQ247)/$AQ$397","v":70.226537216828476},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-06",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,218,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,31.157125106939972,31.157125106939972,null,null,1.7435425868468,84,{"$f":"100*COUNT($AQ$31:AQ248)/$AQ$397","v":70.550161812297731},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-07",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,219,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,24.977154116559024,24.977154116559024,null,null,1.7343223635828999,124,{"$f":"100*COUNT($AQ$31:AQ249)/$AQ$397","v":70.873786407766985},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-08",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,220,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,25.569753144250512,25.569753144250512,null,null,1.7242999461999999,259,{"$f":"100*COUNT($AQ$31:AQ250)/$AQ$397","v":71.19741100323624},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-09",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,221,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,27.583711906569661,27.583711906569661,null,null,1.7237651374559999,274,{"$f":"100*COUNT($AQ$31:AQ251)/$AQ$397","v":71.521035598705495},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-10",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,222,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,23.702538415158074,23.702538415158074,null,null,1.722316445611793,113,{"$f":"100*COUNT($AQ$31:AQ252)/$AQ$397","v":71.84466019417475},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-11",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,223,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,22.680727398282933,22.680727398282933,null,null,1.7144172226331262,255,{"$f":"100*COUNT($AQ$31:AQ253)/$AQ$397","v":72.168284789644019},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-12",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,224,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,21.844547517564422,21.844547517564422,null,null,1.7135963253236763,219,{"$f":"100*COUNT($AQ$31:AQ254)/$AQ$397","v":72.491909385113274},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-13",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,225,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,25.97836378459418,25.97836378459418,null,null,1.7116271153195,293,{"$f":"100*COUNT($AQ$31:AQ255)/$AQ$397","v":72.815533980582529},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-14",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,226,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,35.810459317211631,35.810459317211631,null,null,1.6996821776924718,114,{"$f":"100*COUNT($AQ$31:AQ256)/$AQ$397","v":73.139158576051784},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-15",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,227,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,27.290187005683972,27.290187005683972,null,null,1.6842338794466001,336,{"$f":"100*COUNT($AQ$31:AQ257)/$AQ$397","v":73.462783171521039},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-16",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,228,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,24.006809703917678,24.006809703917678,null,null,1.6838617977657999,283,{"$f":"100*COUNT($AQ$31:AQ258)/$AQ$397","v":73.786407766990294},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-17",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,229,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,25.667384771524045,25.667384771524045,null,null,1.6784716737222036,323,{"$f":"100*COUNT($AQ$31:AQ259)/$AQ$397","v":74.110032362459549},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-18",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,230,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,22.665833550218196,22.665833550218196,null,null,1.6762729623293999,360,{"$f":"100*COUNT($AQ$31:AQ260)/$AQ$397","v":74.433656957928804},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-19",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,231,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,25.97683798581706,25.97683798581706,null,null,1.6724349578636724,135,{"$f":"100*COUNT($AQ$31:AQ261)/$AQ$397","v":74.757281553398059},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-20",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,232,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,26.134865023098122,26.134865023098122,null,null,1.666777429956152,102,{"$f":"100*COUNT($AQ$31:AQ262)/$AQ$397","v":75.080906148867314},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-21",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,233,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,34.96351680404257,34.96351680404257,null,null,1.6619865621369001,341,{"$f":"100*COUNT($AQ$31:AQ263)/$AQ$397","v":75.404530744336569},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-22",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,234,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,29.779485601016447,29.779485601016447,null,null,1.6545155345528,91,{"$f":"100*COUNT($AQ$31:AQ264)/$AQ$397","v":75.728155339805824},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-23",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,235,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,30.567047169457055,30.567047169457055,null,null,1.6487651137320001,170,{"$f":"100*COUNT($AQ$31:AQ265)/$AQ$397","v":76.051779935275079},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-24",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,236,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,23.239181069717869,23.239181069717869,null,null,1.6438625257222363,180,{"$f":"100*COUNT($AQ$31:AQ266)/$AQ$397","v":76.375404530744333},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-25",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,237,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,29.33774947571948,29.33774947571948,null,null,1.6324583292143,226,{"$f":"100*COUNT($AQ$31:AQ267)/$AQ$397","v":76.699029126213588},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-26",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,238,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,26.687088187939118,26.687088187939118,null,null,1.6246218548419999,222,{"$f":"100*COUNT($AQ$31:AQ268)/$AQ$397","v":77.022653721682843},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-27",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,239,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,29.170922615518062,29.170922615518062,null,null,1.6237423975712999,95,{"$f":"100*COUNT($AQ$31:AQ269)/$AQ$397","v":77.346278317152098},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-28",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,240,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,25.255786655456056,25.255786655456056,null,null,1.622112535847849,106,{"$f":"100*COUNT($AQ$31:AQ270)/$AQ$397","v":77.669902912621353},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-29",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,241,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,22.466809496016275,22.466809496016275,null,null,1.6163492359989999,201,{"$f":"100*COUNT($AQ$31:AQ271)/$AQ$397","v":77.993527508090608},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-30",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,242,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,27.422687733871239,27.422687733871239,null,null,1.6118428116645314,280,{"$f":"100*COUNT($AQ$31:AQ272)/$AQ$397","v":78.317152103559877},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-08-31",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,243,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,25.247122912745635,25.247122912745635,null,null,1.5997691195893746,337,{"$f":"100*COUNT($AQ$31:AQ273)/$AQ$397","v":78.640776699029132},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-09-01",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,244,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,26.539577111828592,26.539577111828592,null,null,1.5958157851570001,358,{"$f":"100*COUNT($AQ$31:AQ274)/$AQ$397","v":78.964401294498387},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-09-02",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,245,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,23.465536708030204,23.465536708030204,null,null,1.5929553465490001,2,{"$f":"100*COUNT($AQ$31:AQ275)/$AQ$397","v":79.288025889967642},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-09-03",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,246,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,21.677671919236175,21.677671919236175,null,null,1.5929553465490001,292,{"$f":"100*COUNT($AQ$31:AQ276)/$AQ$397","v":79.611650485436897},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-09-04",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,247,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,23.022967402808007,23.022967402808007,null,null,1.5925739695397001,88,{"$f":"100*COUNT($AQ$31:AQ277)/$AQ$397","v":79.935275080906152},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-09-05",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,248,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,16.34699528185071,16.34699528185071,null,null,1.5918572448999999,186,{"$f":"100*COUNT($AQ$31:AQ278)/$AQ$397","v":80.258899676375407},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-09-06",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,249,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,19.511323043346781,19.511323043346781,null,null,1.5897339187440001,55,{"$f":"100*COUNT($AQ$31:AQ279)/$AQ$397","v":80.582524271844662},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-09-07",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,250,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,16.411683839205779,16.411683839205779,null,null,1.5766662346149218,318,{"$f":"100*COUNT($AQ$31:AQ280)/$AQ$397","v":80.906148867313917},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-09-08",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,251,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,19.956364753025468,19.956364753025468,null,null,1.5749513497500001,17,{"$f":"100*COUNT($AQ$31:AQ281)/$AQ$397","v":81.229773462783172},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-09-09",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,252,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,17.535225662550708,17.535225662550708,null,null,1.5742131688500001,347,{"$f":"100*COUNT($AQ$31:AQ282)/$AQ$397","v":81.553398058252426},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-09-10",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,253,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,24.071647797684502,24.071647797684502,null,null,1.572634736365,37,{"$f":"100*COUNT($AQ$31:AQ283)/$AQ$397","v":81.877022653721681},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-09-11",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,254,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,18.158048260950046,18.158048260950046,null,null,1.5698396731881097,89,{"$f":"100*COUNT($AQ$31:AQ284)/$AQ$397","v":82.200647249190936},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-09-12",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,255,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,19.969336706078956,19.969336706078956,null,null,1.5698396731881097,156,{"$f":"100*COUNT($AQ$31:AQ285)/$AQ$397","v":82.524271844660191},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-09-13",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,256,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,19.475564467896291,19.475564467896291,null,null,1.5648929255277999,205,{"$f":"100*COUNT($AQ$31:AQ286)/$AQ$397","v":82.847896440129446},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-09-14",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,257,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,20.917645917167238,20.917645917167238,null,null,1.5592225332579779,154,{"$f":"100*COUNT($AQ$31:AQ287)/$AQ$397","v":83.171521035598701},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[{"$f":"A287+1","v":"2017-09-15"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"T287+1","v":258},{"$f":"IF(B288=\"\",,Seg1Vol*Seg1Fac/B288*C288)","v":0},{"$f":"Target*0.2828*D288^2.69*C288^0.15*0.933^(E288-5)","v":0},{"$f":"IF(V288=0,,U288/V288)","v":0},{"$f":"IF(B288=\"\",,Seg2Vol*Seg2Fac/B288*F288)","v":0},{"$f":"Target*0.2828*G288^2.69*F288^0.15*0.933^(H288-5)","v":0},{"$f":"IF(Y288=0,,X288/Y288)","v":0},0,0,0,{"$f":"IF(B288=\"\",,Seg4Vol*Seg4Fac/B288*L288)","v":0},{"$f":"Target*0.2828*M288^2.69*L288^0.15*0.933^(N288-5)","v":0},{"$f":"IF(AE288=0,,AD288/AE288)","v":0},{"$f":"IF(B288=\"\",,Seg5Vol*O288*Seg5Fac/B288*P288)","v":0},{"$f":"Target*0.2828*Q288^2.69*P288^0.15*0.933^(R288-5)","v":0},{"$f":"IF(AH288=0,,AG288/AH288)","v":0},{"$f":"W288+Z288+AC288+AF288+AI288","v":0},{"$f":"AJ288*Target","v":0},null,23.70561282131272,23.70561282131272,null,null,1.5587649522847,220,{"$f":"100*COUNT($AQ$31:AQ288)/$AQ$397","v":83.495145631067956},null,{"$f":"$AU$29","v":0},{"$f":"+$AV$29","v":0},null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-09-16",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,259,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,19.399096577006286,19.399096577006286,null,null,1.5587649522847,110,{"$f":"100*COUNT($AQ$31:AQ289)/$AQ$397","v":83.818770226537211},null,0,0,null,{"$f":"$AX$29","v":{"$error":"#DIV/0!"}},{"$f":"+$AY$29","v":{"$error":"#DIV/0!"}}]
["2017-09-17",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,260,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,19.409650360671943,19.409650360671943,null,null,1.558481561,132,{"$f":"100*COUNT($AQ$31:AQ290)/$AQ$397","v":84.142394822006466},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-09-18",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,261,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,23.837458822338057,23.837458822338057,null,null,1.5481598974229001,217,{"$f":"100*COUNT($AQ$31:AQ291)/$AQ$397","v":84.466019417475735},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-09-19",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,262,0,0,0,0,0,0,{"$f":"IF(B292=\"\",,Seg3Vol*Seg3Fac/B292*I292)","v":0},{"$f":"Target*0.2828*J292^2.69*I292^0.15*0.933^(K292-5)","v":0},{"$f":"IF(AB292=0,,AA292/AB292)","v":0},0,0,0,0,0,0,0,0,null,18.931105051830073,18.931105051830073,null,null,1.5436927616130001,176,{"$f":"100*COUNT($AQ$31:AQ292)/$AQ$397","v":84.78964401294499},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-09-20",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,263,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,18.502142553067987,18.502142553067987,null,null,1.5383799959653,308,{"$f":"100*COUNT($AQ$31:AQ293)/$AQ$397","v":85.113268608414245},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-09-21",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,264,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,14.8707187303817,14.8707187303817,null,null,1.525458524174331,271,{"$f":"100*COUNT($AQ$31:AQ294)/$AQ$397","v":85.4368932038835},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-09-22",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,265,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,14.446258485476212,14.446258485476212,null,null,1.5212822823138468,346,{"$f":"100*COUNT($AQ$31:AQ295)/$AQ$397","v":85.760517799352755},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-09-23",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,266,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,16.744881962501644,16.744881962501644,null,null,1.5192819565646793,328,{"$f":"100*COUNT($AQ$31:AQ296)/$AQ$397","v":86.08414239482201},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-09-24",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,267,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,18.354036048480417,18.354036048480417,null,null,1.4951822269849999,32,{"$f":"100*COUNT($AQ$31:AQ297)/$AQ$397","v":86.407766990291265},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-09-25",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,268,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,18.294593863272809,18.294593863272809,null,null,1.4917231891698,301,{"$f":"100*COUNT($AQ$31:AQ298)/$AQ$397","v":86.73139158576052},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-09-26",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,269,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,14.7053323841871,14.7053323841871,null,null,1.4857775584975819,68,{"$f":"100*COUNT($AQ$31:AQ299)/$AQ$397","v":87.055016181229774},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-09-27",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,270,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,18.747240698544786,18.747240698544786,null,null,1.4817273382889999,80,{"$f":"100*COUNT($AQ$31:AQ300)/$AQ$397","v":87.378640776699029},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-09-28",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,271,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,13.337108071588467,13.337108071588467,null,null,1.4767318788113999,268,{"$f":"100*COUNT($AQ$31:AQ301)/$AQ$397","v":87.702265372168284},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-09-29",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,272,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,11.910448701294413,11.910448701294413,null,null,1.4756262361362,278,{"$f":"100*COUNT($AQ$31:AQ302)/$AQ$397","v":88.025889967637539},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-09-30",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,273,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,14.723840851946036,14.723840851946036,null,null,1.46662124435,272,{"$f":"100*COUNT($AQ$31:AQ303)/$AQ$397","v":88.349514563106794},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-01",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,274,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,14.577186102379018,14.577186102379018,null,null,1.4632865822726646,130,{"$f":"100*COUNT($AQ$31:AQ304)/$AQ$397","v":88.673139158576049},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-02",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,275,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,10.775198437066035,10.775198437066035,null,null,1.4541487739779999,331,{"$f":"100*COUNT($AQ$31:AQ305)/$AQ$397","v":88.996763754045304},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-03",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,276,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,12.944693169172549,12.944693169172549,null,null,1.4541163295549,54,{"$f":"100*COUNT($AQ$31:AQ306)/$AQ$397","v":89.320388349514559},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-04",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,277,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.7875614863337237,9.7875614863337237,null,null,1.4526563442680001,41,{"$f":"100*COUNT($AQ$31:AQ307)/$AQ$397","v":89.644012944983814},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-05",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,278,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,10.449129354405535,10.449129354405535,null,null,1.4471158967219999,233,{"$f":"100*COUNT($AQ$31:AQ308)/$AQ$397","v":89.967637540453069},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-06",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,279,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.9227683926475887,9.9227683926475887,null,null,1.4362576529566,290,{"$f":"100*COUNT($AQ$31:AQ309)/$AQ$397","v":90.291262135922324},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-07",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,280,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,6.4004799689501581,6.4004799689501581,null,null,1.4321667843300001,94,{"$f":"100*COUNT($AQ$31:AQ310)/$AQ$397","v":90.614886731391579},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-08",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,281,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,11.303400397202443,11.303400397202443,null,null,1.4291438418219999,298,{"$f":"100*COUNT($AQ$31:AQ311)/$AQ$397","v":90.938511326860848},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-09",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,282,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.0935429204629887,9.0935429204629887,null,null,1.397228554375,53,{"$f":"100*COUNT($AQ$31:AQ312)/$AQ$397","v":91.262135922330103},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-10",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,283,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,8.0848807277442418,8.0848807277442418,null,null,1.394845315,225,{"$f":"100*COUNT($AQ$31:AQ313)/$AQ$397","v":91.585760517799358},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-11",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,284,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.0460931212691573,9.0460931212691573,null,null,1.3939478967985415,294,{"$f":"100*COUNT($AQ$31:AQ314)/$AQ$397","v":91.909385113268613},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-12",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,285,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,7.5335885909743405,7.5335885909743405,null,null,1.3935184181972966,289,{"$f":"100*COUNT($AQ$31:AQ315)/$AQ$397","v":92.233009708737868},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-13",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,286,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,7.4249791577233397,7.4249791577233397,null,null,1.3863181146968593,251,{"$f":"100*COUNT($AQ$31:AQ316)/$AQ$397","v":92.556634304207122},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-14",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,287,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,7.6656813718540624,7.6656813718540624,null,null,1.3821318797582001,207,{"$f":"100*COUNT($AQ$31:AQ317)/$AQ$397","v":92.880258899676377},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-15",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,288,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,7.5596427518708875,7.5596427518708875,null,null,1.3743237196666001,361,{"$f":"100*COUNT($AQ$31:AQ318)/$AQ$397","v":93.203883495145632},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-16",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,289,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,10.074259088122844,10.074259088122844,null,null,1.3725782639396304,175,{"$f":"100*COUNT($AQ$31:AQ319)/$AQ$397","v":93.527508090614887},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-17",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,290,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,8.3414848149228185,8.3414848149228185,null,null,1.3682191124180001,184,{"$f":"100*COUNT($AQ$31:AQ320)/$AQ$397","v":93.851132686084142},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-18",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,291,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,6.6490323508698816,6.6490323508698816,null,null,1.3677393166828,224,{"$f":"100*COUNT($AQ$31:AQ321)/$AQ$397","v":94.174757281553397},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-19",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,292,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,10.98646993012578,10.98646993012578,null,null,1.3351296534935999,282,{"$f":"100*COUNT($AQ$31:AQ322)/$AQ$397","v":94.498381877022652},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-20",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,293,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,8.4218413745003442,8.4218413745003442,null,null,1.3339983719516,313,{"$f":"100*COUNT($AQ$31:AQ323)/$AQ$397","v":94.822006472491907},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-21",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,294,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.6535469859560958,9.6535469859560958,null,null,1.3291415831237523,246,{"$f":"100*COUNT($AQ$31:AQ324)/$AQ$397","v":95.145631067961162},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-22",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,295,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,12.506773987049232,12.506773987049232,null,null,1.3183114623832852,42,{"$f":"100*COUNT($AQ$31:AQ325)/$AQ$397","v":95.469255663430417},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-23",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,296,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,8.7006681244952304,8.7006681244952304,null,null,1.2966278123684001,22,{"$f":"100*COUNT($AQ$31:AQ326)/$AQ$397","v":95.792880258899672},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-24",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,297,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,11.269785845424208,11.269785845424208,null,null,1.2911673799372001,62,{"$f":"100*COUNT($AQ$31:AQ327)/$AQ$397","v":96.116504854368927},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-25",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,298,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,7.4055627649984963,7.4055627649984963,null,null,1.2881131798330001,28,{"$f":"100*COUNT($AQ$31:AQ328)/$AQ$397","v":96.440129449838182},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-26",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,299,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,8.3125016368269993,8.3125016368269993,null,null,1.2854724616933,213,{"$f":"100*COUNT($AQ$31:AQ329)/$AQ$397","v":96.763754045307437},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-27",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,300,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.6143151195498859,9.6143151195498859,null,null,1.2695556479500001,97,{"$f":"100*COUNT($AQ$31:AQ330)/$AQ$397","v":97.087378640776706},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-28",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,301,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.1287265848492076,9.1287265848492076,null,null,1.23664188443,19,{"$f":"100*COUNT($AQ$31:AQ331)/$AQ$397","v":97.411003236245961},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-29",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,302,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,8.7144292607850851,8.7144292607850851,null,null,1.235435733878,344,{"$f":"100*COUNT($AQ$31:AQ332)/$AQ$397","v":97.734627831715216},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-30",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,303,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,6.6923704115340916,6.6923704115340916,null,null,1.2258479992169999,287,{"$f":"100*COUNT($AQ$31:AQ333)/$AQ$397","v":98.05825242718447},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-10-31",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,304,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,6.7625223105490067,6.7625223105490067,null,null,1.1886664371444999,260,{"$f":"100*COUNT($AQ$31:AQ334)/$AQ$397","v":98.381877022653725},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-11-01",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,305,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,7.5854070274490573,7.5854070274490573,null,null,1.1886664371444999,34,{"$f":"100*COUNT($AQ$31:AQ335)/$AQ$397","v":98.70550161812298},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-11-02",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,306,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,8.4491866668346471,8.4491866668346471,null,null,1.1466324362810001,129,{"$f":"100*COUNT($AQ$31:AQ336)/$AQ$397","v":99.029126213592235},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-11-03",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,307,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,6.636447171449138,6.636447171449138,null,null,1.1262743182266,276,{"$f":"100*COUNT($AQ$31:AQ337)/$AQ$397","v":99.35275080906149},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-11-04",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,308,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,6.0562342491220402,6.0562342491220402,null,null,1.124963745378498,232,{"$f":"100*COUNT($AQ$31:AQ338)/$AQ$397","v":99.676375404530745},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-11-05",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,309,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,9.6722708710524277,9.6722708710524277,null,null,1.124963745378498,101,{"$f":"100*COUNT($AQ$31:AQ339)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-11-06",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,310,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,7.2453699573927359,7.2453699573927359,null,null,null,359,{"$f":"100*COUNT($AQ$31:AQ340)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-11-07",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,311,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,7.7487791279898222,7.7487791279898222,null,null,null,147,{"$f":"100*COUNT($AQ$31:AQ341)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-11-08",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,312,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,7.6135595542072254,7.6135595542072254,null,null,null,25,{"$f":"100*COUNT($AQ$31:AQ342)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-11-09",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,313,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,7.4677729112130944,7.4677729112130944,null,null,null,7,{"$f":"100*COUNT($AQ$31:AQ343)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-11-10",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,314,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,8.4523802322388537,8.4523802322388537,null,null,null,165,{"$f":"100*COUNT($AQ$31:AQ344)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-11-11",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,315,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,6.0297618585959762,6.0297618585959762,null,null,null,20,{"$f":"100*COUNT($AQ$31:AQ345)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-11-12",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,316,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,7.212309231426552,7.212309231426552,null,null,null,241,{"$f":"100*COUNT($AQ$31:AQ346)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-11-13",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,317,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.4957678987851448,5.4957678987851448,null,null,null,112,{"$f":"100*COUNT($AQ$31:AQ347)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-11-14",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,318,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.9840977241563449,5.9840977241563449,null,null,null,96,{"$f":"100*COUNT($AQ$31:AQ348)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-11-15",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,319,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.8995726050691379,5.8995726050691379,null,null,null,14,{"$f":"100*COUNT($AQ$31:AQ349)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-11-16",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,320,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.487175595272058,5.487175595272058,null,null,null,111,{"$f":"100*COUNT($AQ$31:AQ350)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-11-17",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,321,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,6.037015654439859,6.037015654439859,null,null,null,314,{"$f":"100*COUNT($AQ$31:AQ351)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[{"$f":"A351+1","v":"2017-11-18"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"T351+1","v":322},{"$f":"IF(B352=\"\",,Seg1Vol*Seg1Fac/B352*C352)","v":0},{"$f":"Target*0.2828*D352^2.69*C352^0.15*0.933^(E352-5)","v":0},{"$f":"IF(V352=0,,U352/V352)","v":0},{"$f":"IF(B352=\"\",,Seg2Vol*Seg2Fac/B352*F352)","v":0},{"$f":"Target*0.2828*G352^2.69*F352^0.15*0.933^(H352-5)","v":0},{"$f":"IF(Y352=0,,X352/Y352)","v":0},0,0,0,{"$f":"IF(B352=\"\",,Seg4Vol*Seg4Fac/B352*L352)","v":0},{"$f":"Target*0.2828*M352^2.69*L352^0.15*0.933^(N352-5)","v":0},{"$f":"IF(AE352=0,,AD352/AE352)","v":0},{"$f":"IF(B352=\"\",,Seg5Vol*O352*Seg5Fac/B352*P352)","v":0},{"$f":"Target*0.2828*Q352^2.69*P352^0.15*0.933^(R352-5)","v":0},{"$f":"IF(AH352=0,,AG352/AH352)","v":0},{"$f":"W352+Z352+AC352+AF352+AI352","v":0},{"$f":"AJ352*Target","v":0},null,5.8212731145291388,5.8212731145291388,null,null,null,329,{"$f":"100*COUNT($AQ$31:AQ352)/$AQ$397","v":100},null,{"$f":"$AU$29","v":0},{"$f":"+$AV$29","v":0},null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-11-19",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,323,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,6.1538185263594212,6.1538185263594212,null,null,null,81,{"$f":"100*COUNT($AQ$31:AQ353)/$AQ$397","v":100},null,0,0,null,{"$f":"$AX$29","v":{"$error":"#DIV/0!"}},{"$f":"+$AY$29","v":{"$error":"#DIV/0!"}}]
["2017-11-20",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,324,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,4.0920751698816797,4.0920751698816797,null,null,null,216,{"$f":"100*COUNT($AQ$31:AQ354)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-11-21",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,325,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,4.1508976639554858,4.1508976639554858,null,null,null,296,{"$f":"100*COUNT($AQ$31:AQ355)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-11-22",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,326,0,0,0,0,0,0,{"$f":"IF(B356=\"\",,Seg3Vol*Seg3Fac/B356*I356)","v":0},{"$f":"Target*0.2828*J356^2.69*I356^0.15*0.933^(K356-5)","v":0},{"$f":"IF(AB356=0,,AA356/AB356)","v":0},0,0,0,0,0,0,0,0,null,4.9365309091799645,4.9365309091799645,null,null,null,169,{"$f":"100*COUNT($AQ$31:AQ356)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-11-23",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,327,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.0646429225171081,5.0646429225171081,null,null,null,353,{"$f":"100*COUNT($AQ$31:AQ357)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-11-24",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,328,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,4.1619646806309909,4.1619646806309909,null,null,null,362,{"$f":"100*COUNT($AQ$31:AQ358)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-11-25",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,329,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.2566813026841137,5.2566813026841137,null,null,null,160,{"$f":"100*COUNT($AQ$31:AQ359)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-11-26",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,330,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,4.7982515041432521,4.7982515041432521,null,null,null,64,{"$f":"100*COUNT($AQ$31:AQ360)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-11-27",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,331,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,6.0917214941309359,6.0917214941309359,null,null,null,30,{"$f":"100*COUNT($AQ$31:AQ361)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-11-28",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,332,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,6.3986782027554936,6.3986782027554936,null,null,null,138,{"$f":"100*COUNT($AQ$31:AQ362)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-11-29",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,333,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.1412277048678661,5.1412277048678661,null,null,null,266,{"$f":"100*COUNT($AQ$31:AQ363)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[{"$f":"A363+1","v":"2017-11-30"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,334,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,4.9803689294744888,4.9803689294744888,null,null,null,221,{"$f":"100*COUNT($AQ$31:AQ364)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[{"$f":"A364+1","v":"2017-12-01"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,335,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.5004105894131294,5.5004105894131294,null,null,null,126,{"$f":"100*COUNT($AQ$31:AQ365)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-02",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,336,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.7216051700699637,5.7216051700699637,null,null,null,265,{"$f":"100*COUNT($AQ$31:AQ366)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-03",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,337,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.0129227912966385,5.0129227912966385,null,null,null,200,{"$f":"100*COUNT($AQ$31:AQ367)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-04",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,338,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.922243158945637,5.922243158945637,null,null,null,121,{"$f":"100*COUNT($AQ$31:AQ368)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-05",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,339,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.5591188611132178,5.5591188611132178,null,null,null,334,{"$f":"100*COUNT($AQ$31:AQ369)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-06",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,340,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,4.3839606522520596,4.3839606522520596,null,null,null,269,{"$f":"100*COUNT($AQ$31:AQ370)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-07",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,341,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.1924062289305626,5.1924062289305626,null,null,null,365,{"$f":"100*COUNT($AQ$31:AQ371)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-08",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,342,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.4173172591850793,5.4173172591850793,null,null,null,93,{"$f":"100*COUNT($AQ$31:AQ372)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-09",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,343,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.2856742914943329,5.2856742914943329,null,null,null,167,{"$f":"100*COUNT($AQ$31:AQ373)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-10",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,344,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,3.2450461215788891,3.2450461215788891,null,null,null,300,{"$f":"100*COUNT($AQ$31:AQ374)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-11",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,345,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,2.2660554940886648,2.2660554940886648,null,null,null,338,{"$f":"100*COUNT($AQ$31:AQ375)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-12",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,346,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,2.6505616100072844,2.6505616100072844,null,null,null,188,{"$f":"100*COUNT($AQ$31:AQ376)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-13",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,347,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,3.8582777287744987,3.8582777287744987,null,null,null,330,{"$f":"100*COUNT($AQ$31:AQ377)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-14",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,348,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,3.4872351831940378,3.4872351831940378,null,null,null,363,{"$f":"100*COUNT($AQ$31:AQ378)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-15",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,349,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,3.4569723820622773,3.4569723820622773,null,null,null,74,{"$f":"100*COUNT($AQ$31:AQ379)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-16",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,350,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,4.2871985524161333,4.2871985524161333,null,null,null,87,{"$f":"100*COUNT($AQ$31:AQ380)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-17",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,351,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,4.6082905170441375,4.6082905170441375,null,null,null,262,{"$f":"100*COUNT($AQ$31:AQ381)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-18",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,352,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,3.9480940923982724,3.9480940923982724,null,null,null,295,{"$f":"100*COUNT($AQ$31:AQ382)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-19",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,353,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,3.4728487132292241,3.4728487132292241,null,null,null,31,{"$f":"100*COUNT($AQ$31:AQ383)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-20",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,354,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,3.5046404256716306,3.5046404256716306,null,null,null,345,{"$f":"100*COUNT($AQ$31:AQ384)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-21",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,355,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,3.7136402536894919,3.7136402536894919,null,null,null,196,{"$f":"100*COUNT($AQ$31:AQ385)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-22",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,356,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,3.8423555138950136,3.8423555138950136,null,null,null,107,{"$f":"100*COUNT($AQ$31:AQ386)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-23",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,357,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,4.0608752269869468,4.0608752269869468,null,null,null,229,{"$f":"100*COUNT($AQ$31:AQ387)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-24",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,358,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,3.2884002537076,3.2884002537076,null,null,null,319,{"$f":"100*COUNT($AQ$31:AQ388)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-25",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,359,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,4.3418633080525959,4.3418633080525959,null,null,null,261,{"$f":"100*COUNT($AQ$31:AQ389)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-26",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,360,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,3.8472793537220049,3.8472793537220049,null,null,null,6,{"$f":"100*COUNT($AQ$31:AQ390)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-27",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,361,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,4.0108305996419196,4.0108305996419196,null,null,null,153,{"$f":"100*COUNT($AQ$31:AQ391)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-28",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,362,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,3.264822678817398,3.264822678817398,null,null,null,119,{"$f":"100*COUNT($AQ$31:AQ392)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-29",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,363,{"$f":"IF(B393=\"\",,Seg1Vol*Seg1Fac/B393*C393)","v":0},{"$f":"Target*0.2828*D393^2.69*C393^0.15*0.933^(E393-5)","v":0},{"$f":"IF(V393=0,,U393/V393)","v":0},{"$f":"IF(B393=\"\",,Seg2Vol*Seg2Fac/B393*F393)","v":0},{"$f":"Target*0.2828*G393^2.69*F393^0.15*0.933^(H393-5)","v":0},{"$f":"IF(Y393=0,,X393/Y393)","v":0},{"$f":"IF(B393=\"\",,Seg3Vol*Seg3Fac/B393*I393)","v":0},{"$f":"Target*0.2828*J393^2.69*I393^0.15*0.933^(K393-5)","v":0},{"$f":"IF(AB393=0,,AA393/AB393)","v":0},{"$f":"IF(B393=\"\",,Seg4Vol*Seg4Fac/B393*L393)","v":0},{"$f":"Target*0.2828*M393^2.69*L393^0.15*0.933^(N393-5)","v":0},{"$f":"IF(AE393=0,,AD393/AE393)","v":0},0,{"$f":"Target*0.2828*Q393^2.69*P393^0.15*0.933^(R393-5)","v":0},{"$f":"IF(AH393=0,,AG393/AH393)","v":0},{"$f":"W393+Z393+AC393+AF393+AI393","v":0},0,null,4.6083291878494972,4.6083291878494972,null,null,null,null,null,null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-30",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,364,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,3.757044158316587,3.757044158316587,null,null,null,136,{"$f":"100*COUNT($AQ$31:AQ394)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2017-12-31",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,365,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,3.5821967182284391,3.5821967182284391,null,null,null,48,{"$f":"100*COUNT($AQ$31:AQ395)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
["2018-01-01",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,366,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,null,null,null,null,null,38,{"$f":"100*COUNT($AQ$31:AQ396)/$AQ$397","v":100},null,0,0,null,{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"COUNT(CombSort)","v":309},null,null,null,null,0,null,null,{"$f":"+$AV$29","v":0}]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"422/13","v":32.46153846153846}]

{"sheet":"Disinfection Summary","index":10,"n_rows":68,"n_cols":9,"rows_kept":68,"cut":false,"hidden":true,"merged":[[51,2,51,4],[52,2,52,3]]}
[]
[null,null,{"$f":"Menu!C5","v":"Watertown Waterworks"},null,null,null,null,null,"Disinfection Summary Report"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,"ANNUAL DATA",null,null,"Avg","Min","Max"]
[]
[null,null,"Inactivation Ratio (M/R)",null,null,{"$f":"AVERAGE(YearPlotOne)","v":14.681570135975296},{"$f":"MIN(YearPlotOne)","v":2.2660554940886648},{"$f":"MAX(YearPlotOne)","v":46.163748528481143}]
[null,null,"Giardia Inactivation (log)",null,null,{"$f":"AVERAGE(YearPlotTwo)","v":14.681570135975296},{"$f":"MIN(YearPlotTwo)","v":2.2660554940886648},{"$f":"MAX(YearPlotTwo)","v":46.163748528481143}]
[]
[]
[null,null,"MONTHLY","Avg Ratio","Min Ratio","Max Ratio","Avg Inact","Min Inact","Max Inact"]
[null,null,"DATA","M/R","M/R","M/R","Log","Log","Log"]
[null,null,"2017-01-01",5.240217107729249,3.8832578902629686,6.5868283363771098,5.240217107729249,3.8832578902629686,6.5868283363771098]
[null,null,"2017-02-01",8.0596403125202531,5.0358032431088624,10.712972161043931,8.0596403125202531,5.0358032431088624,10.712972161043931]
[null,null,"2017-03-01",9.9664809755221473,6.7734621782225375,13.925095635786031,9.9664809755221473,6.7734621782225375,13.925095635786031]
[null,null,"2017-04-01",11.153741369354979,8.6172910087134511,15.569024086377407,11.153741369354979,8.6172910087134511,15.569024086377407]
[null,null,"2017-05-01",17.19474973886555,10.230686477259443,25.004872554680396,17.19474973886555,10.230686477259443,25.004872554680396]
[null,null,"2017-06-01",26.391379690785072,16.469539812353315,44.263525540285755,26.391379690785072,16.469539812353315,44.263525540285755]
[null,null,"2017-07-01",31.478779218159776,20.253583764625553,40.702110566583038,31.478779218159776,20.253583764625553,40.702110566583038]
[null,null,"2017-08-01",27.692274577212203,12.974211921333428,46.163748528481143,27.692274577212203,12.974211921333428,46.163748528481143]
[null,null,"2017-09-01",18.899303828518672,11.910448701294413,26.539577111828592,18.899303828518672,11.910448701294413,26.539577111828592]
[null,null,"2017-10-01",9.2194553722779116,6.4004799689501581,14.577186102379018,9.2194553722779116,6.4004799689501581,14.577186102379018]
[null,null,"2017-11-01",6.2040413487268005,4.0920751698816797,9.6722708710524277,6.2040413487268005,4.0920751698816797,9.6722708710524277]
[null,null,"2017-12-01",4.1644682927765535,2.2660554940886648,5.922243158945637,4.1644682927765535,2.2660554940886648,5.922243158945637]
[]
[]
[null,null,"ANNUAL DATA",null,null,"Average","Min","Max","STDEV"]
[]
[null,null,{"$f":"'DataEntryValues(CT)'!C28&\" Cl2\"","v":"Segment 1 -  Cl2"},null,null,{"$f":"IF(SUM(Seg1Cl2)=0,,AVERAGE(Seg1Cl2))","v":0},{"$f":"MIN(Seg1Cl2)","v":0},{"$f":"MAX(Seg1Cl2)","v":0},{"$f":"IF(SUM(Seg1Cl2)=0,,STDEV(Seg1Cl2))","v":0}]
[null,null,{"$f":"'DataEntryValues(CT)'!C28&\" pH\"","v":"Segment 1 -  pH"},null,null,{"$f":"IF(SUM(Seg1pH)=0,,MEDIAN(Seg1pH))","v":0},{"$f":"MIN(Seg1pH)","v":0},{"$f":"MAX(Seg1pH)","v":0},{"$f":"IF(SUM(Seg1pH)=0,,STDEV(Seg1pH))","v":0}]
[null,null,{"$f":"'DataEntryValues(CT)'!C28&\" Temp.\"","v":"Segment 1 -  Temp."},null,null,{"$f":"IF(SUM(Seg1Temp)=0,,AVERAGE(Seg1Temp))","v":0},{"$f":"MIN(Seg1Temp)","v":0},{"$f":"MAX(Seg1Temp)","v":0},{"$f":"IF(SUM(Seg1Temp)=0,,STDEV(Seg1Temp))","v":0}]
[null,null,{"$f":"'DataEntryValues(CT)'!F28&\" Cl2\"","v":"Segment 2 -  Cl2"},null,null,{"$f":"IF(SUM(seg2cl2)=0,,AVERAGE(seg2cl2))","v":0},{"$f":"MIN(seg2cl2)","v":0},{"$f":"MAX(seg2cl2)","v":0},{"$f":"IF(SUM(seg2cl2)=0,,STDEV(seg2cl2))","v":0}]
[null,null,{"$f":"'DataEntryValues(CT)'!F28&\" pH\"","v":"Segment 2 -  pH"},null,null,{"$f":"IF(SUM(Seg2pH)=0,,MEDIAN(Seg2pH))","v":0},{"$f":"MIN(Seg2pH)","v":0},{"$f":"MAX(Seg2pH)","v":0},{"$f":"IF(SUM(Seg2pH)=0,,STDEV(Seg2pH))","v":0}]
[null,null,{"$f":"'DataEntryValues(CT)'!F28&\" Temp.\"","v":"Segment 2 -  Temp."},null,null,{"$f":"IF(SUM(seg2temp)=0,,AVERAGE(seg2temp))","v":0},{"$f":"MIN(seg2temp)","v":0},{"$f":"MAX(seg2temp)","v":0},{"$f":"IF(SUM(seg2temp)=0,,STDEV(seg2temp))","v":0}]
[null,null,{"$f":"'DataEntryValues(CT)'!I28&\" Cl2\"","v":"Segment 3 -  Cl2"},null,null,{"$f":"IF(SUM(seg3cl2)=0,,AVERAGE(seg3cl2))","v":0},{"$f":"MIN(seg3cl2)","v":0},{"$f":"MAX(seg3cl2)","v":0},{"$f":"IF(SUM(seg3cl2)=0,,STDEV(seg3cl2))","v":0}]
[null,null,{"$f":"'DataEntryValues(CT)'!I28&\" pH\"","v":"Segment 3 -  pH"},null,null,{"$f":"IF(SUM(seg3ph)=0,,MEDIAN(seg3ph))","v":0},{"$f":"MIN(seg3ph)","v":0},{"$f":"MAX(seg3ph)","v":0},{"$f":"IF(SUM(seg3ph)=0,,STDEV(seg3ph))","v":0}]
[null,null,{"$f":"'DataEntryValues(CT)'!I28&\" Temp.\"","v":"Segment 3 -  Temp."},null,null,{"$f":"IF(SUM(seg3temp)=0,,AVERAGE(seg3temp))","v":0},{"$f":"MIN(seg3temp)","v":0},{"$f":"MAX(seg3temp)","v":0},{"$f":"IF(SUM(seg3temp)=0,,STDEV(seg3temp))","v":0}]
[null,null,{"$f":"'DataEntryValues(CT)'!L28&\" Cl2\"","v":"Segment 4 -  Cl2"},null,null,{"$f":"IF(SUM(seg4cl2)=0,,AVERAGE(seg4cl2))","v":0},{"$f":"MIN(seg4cl2)","v":0},{"$f":"MAX(seg4cl2)","v":0},{"$f":"IF(SUM(seg4cl2)=0,,STDEV(seg4cl2))","v":0}]
[null,null,{"$f":"'DataEntryValues(CT)'!L28&\" pH\"","v":"Segment 4 -  pH"},null,null,{"$f":"IF(SUM(seg4ph)=0,,MEDIAN(seg4ph))","v":0},{"$f":"MIN(seg4ph)","v":0},{"$f":"MAX(seg4ph)","v":0},{"$f":"IF(SUM(seg4ph)=0,,STDEV(seg4ph))","v":0}]
[null,null,{"$f":"'DataEntryValues(CT)'!L28&\" Temp.\"","v":"Segment 4 -  Temp."},null,null,{"$f":"IF(SUM(seg4temp)=0,,AVERAGE(seg4temp))","v":0},{"$f":"MIN(seg4temp)","v":0},{"$f":"MAX(seg4temp)","v":0},{"$f":"IF(SUM(seg4temp)=0,,STDEV(seg4temp))","v":0}]
[null,null,{"$f":"'DataEntryValues(CT)'!O28&\" Cl2\"","v":"Segment 5 -  Cl2"},null,null,{"$f":"IF(SUM(seg5cl2)=0,,AVERAGE(seg5cl2))","v":0},{"$f":"MIN(seg5cl2)","v":0},{"$f":"MAX(seg5cl2)","v":0},{"$f":"IF(SUM(seg5cl2)=0,,STDEV(seg5cl2))","v":0}]
[null,null,{"$f":"'DataEntryValues(CT)'!O28&\" pH\"","v":"Segment 5 -  pH"},null,null,{"$f":"IF(SUM(seg5ph)=0,,MEDIAN(seg5ph))","v":0},{"$f":"MIN(seg5ph)","v":0},{"$f":"MAX(seg5ph)","v":0},{"$f":"IF(SUM(seg5ph)=0,,STDEV(seg5ph))","v":0}]
[null,null,{"$f":"'DataEntryValues(CT)'!O28&\" Temp.\"","v":"Segment 5 -  Temp."},null,null,{"$f":"IF(SUM(seg5temp)=0,,AVERAGE(seg5temp))","v":0},{"$f":"MIN(seg5temp)","v":0},{"$f":"MAX(seg5temp)","v":0},{"$f":"IF(SUM(seg5temp)=0,,STDEV(seg5temp))","v":0}]

{"sheet":"Total Inact Ratio","index":11,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":true,"merged":[]}

{"sheet":"Segment Inact Ratio","index":12,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":true,"merged":[]}

{"sheet":"pH Summary","index":13,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":true,"merged":[]}

{"sheet":"ChloramineCT","index":14,"n_rows":28,"n_cols":12,"rows_kept":28,"cut":false,"hidden":true,"merged":[]}
[]
[null,null,"CT Values for Inactivation of Giardia Cysts by Chloramine"]
[]
[null,null,null,1,5,10,15,20,25]
[null,null,0.5,635,365,310,250,185,125]
[null,null,1,1270,735,615,500,370,250]
[null,null,1.5,1900,1100,930,750,550,375]
[null,null,2,2535,1470,1230,1000,735,500]
[null,null,2.5,3170,1830,1540,1250,915,625]
[null,null,3,3800,2200,1850,1500,1100,750]
[]
[null,null,"Inactivation rate (k) values (log/CT)"]
[null,null,null,1,5,10,15,20,25]
[null,null,0.5,{"$f":"$C$14/D5","v":7.874015748031496E-4},1.3698630136986301E-3,1.6129032258064516E-3,2E-3,2.7027027027027029E-3,4.0000000000000001E-3]
[null,null,1,{"$f":"$C$15/D6","v":7.874015748031496E-4},1.3605442176870747E-3,1.6260162601626016E-3,2E-3,2.7027027027027029E-3,4.0000000000000001E-3]
[null,null,1.5,{"$f":"$C$16/D7","v":7.894736842105263E-4},1.3636363636363637E-3,1.6129032258064516E-3,2E-3,2.7272727272727275E-3,4.0000000000000001E-3]
[null,null,2,{"$f":"$C$17/D8","v":7.8895463510848124E-4},1.3605442176870747E-3,1.6260162601626016E-3,2E-3,2.7210884353741495E-3,4.0000000000000001E-3]
[null,null,2.5,{"$f":"$C$18/D9","v":7.8864353312302837E-4},1.366120218579235E-3,1.6233766233766235E-3,2E-3,2.7322404371584699E-3,4.0000000000000001E-3]
[null,null,3,{"$f":"$C$19/D10","v":7.894736842105263E-4},1.3636363636363637E-3,1.6216216216216215E-3,2E-3,2.7272727272727275E-3,4.0000000000000001E-3]
[null,null,"average",{"$f":"AVERAGE(D14:D19)","v":7.8855811437647701E-4},1.3640573991541237E-3,1.6204728694893921E-3,2E-3,2.7188799554139133E-3,4.0000000000000001E-3]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,"Temp.","Log"]
[null,null,null,null,null,null,null,null,null,null,5,0.5]
[]
[null,null,null,null,null,null,null,null,null,null,"CT"]
[null,null,null,null,null,null,null,null,null,null,{"$f":"L25/(1.383*10^-9*K25^5-1.033*10^-7*K25^4+3.206*10^-6*K25^3-4.471*10^-5*K25^2+3.278*10^-4*K25+5.024*10^-4)","v":366.52608863975297}]

{"sheet":"ClO2-CT","index":15,"n_rows":28,"n_cols":11,"rows_kept":28,"cut":false,"hidden":true,"merged":[]}
[]
[null,"CT Values for Inactivation of Giardia Cysts by Chlorine Dioxide"]
[]
[null,null,1,5,10,15,20,25]
[null,0.5,10,4.3,4,3.2,2.5,2]
[null,1,21,8.6999999999999993,7.7,6.3,5,3.7]
[null,1.5,32,13,12,10,7.5,5.5]
[null,2,42,17,15,13,10,7.3]
[null,2.5,52,22,19,16,13,9]
[null,3,63,26,23,19,15,11]
[]
[null,"Inactivation rate (k) values (log/CT)"]
[null,null,1,5,10,15,20,25]
[null,0.5,{"$f":"$B$14/C5","v":0.05},0.11627906976744186,0.125,0.15625,0.2,0.25]
[null,1,{"$f":"$B$15/C6","v":4.7619047619047616E-2},0.1149425287356322,0.12987012987012986,0.15873015873015872,0.2,0.27027027027027023]
[null,1.5,{"$f":"$B$16/C7","v":4.6875E-2},0.11538461538461539,0.125,0.15,0.2,0.27272727272727271]
[null,2,{"$f":"$B$17/C8","v":4.7619047619047616E-2},0.11764705882352941,0.13333333333333333,0.15384615384615385,0.2,0.27397260273972601]
[null,2.5,{"$f":"$B$18/C9","v":4.807692307692308E-2},0.11363636363636363,0.13157894736842105,0.15625,0.19230769230769232,0.27777777777777779]
[null,3,{"$f":"$B$19/C10","v":4.7619047619047616E-2},0.11538461538461539,0.13043478260869565,0.15789473684210525,0.2,0.27272727272727271]
[null,"average",{"$f":"AVERAGE(C14:C19)","v":4.7968177655677652E-2},0.11554570862203299,0.12920286553009666,0.15549517490306963,0.19871794871794871,0.26957919937371988]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,"Temp.","Log"]
[null,null,null,null,null,null,null,null,null,5,1.5]
[]
[null,null,null,null,null,null,null,null,null,"CT"]
[null,null,null,null,null,null,null,null,null,{"$f":"K25/(2.913*10^-7*J25^5-2.142*10^-5*J25^4+6.034*10^-4*J25^3-7.739*10^-3*J25^2+4.774*10^-2*J25+7.389*10^-3)","v":12.980066403856375}]

{"sheet":"AllDataSort","index":16,"n_rows":373,"n_cols":22,"rows_kept":373,"cut":false,"hidden":true,"merged":[[4,6,4,8],[4,9,4,11],[4,12,4,14],[4,15,4,17]]}
[]
[null,null,null,null,null,{"$f":"'DataEntryValues(CT)'!F3","v":"Watertown"},null,null,null,"2017-02-01"]
[null,null,null,null,null,"Cell to identify if year is a leap year or not.",null,null,null,{"$f":"IF(MOD(YEAR(J2)/4,1)=0,1,2)","v":2}]
[null,null,null,null,"Annual Data"]
[null,null,null,null,null,null,"Segment 1",null,null,"Segment 2",null,null,"Segment 3",null,null,"Segment 4",null,null,"Segment 5"]
[null,null,null,null,"Date","Flow","Residual","pH","Temp.","Residual","pH","Temp.","Residual","pH","Temp.","Residual","pH","Temp.","Depth","Residual","pH","Temp."]
["FebValue","FebFind",null,null,null,"gpm","mg/L",null,"C","mg/L",null,"C","mg/L",null,"C","mg/L",null,"C","ft","mg/L",null,"C"]
[0,{"$f":"IF(MONTH(E8)=2,\"feb\",)","v":0},{"$f":"MONTH(E8)","v":1},1,"2017-01-01",4128.4861111111113,1.1499999999999999,7.13,5.5,0.64,7.06,5.2,null,null,null,null,null,null,13.7,0.71,7.2,4.9000000000000004]
[0,0,{"$f":"MONTH(E9)","v":1},1,"2017-01-02",3944.661111111111,1.59,7.05,6.1,0.7,7.11,6.2,null,null,null,null,null,null,13.6,0.87,7.3,5.2]
[0,0,1,1,"2017-01-03",3980.7180555555556,1.34,6.95,5.2,0.76,7.06,5.3,null,null,null,null,null,null,13.3,0.75,7.2,5.6]
[0,0,1,1,"2017-01-04",3847.9569444444446,1.64,7.09,5.6,0.88,7.1,5.6,null,null,null,null,null,null,11.4,0.8,7.1,5.8]
[0,0,1,1,"2017-01-05",4073.4756944444443,1.6,6.9,5.5,0.5,6.8,5.5,null,null,null,null,null,null,13.7,0.8,7.1,5.5]
[0,0,1,1,"2017-01-06",3936.1291666666666,1.4,7.17,6.2,0.77,7.09,6,null,null,null,null,null,null,14.5,0.7,7.2,4.7]
[0,0,1,1,"2017-01-07",3894.0187500000002,1.6,7.07,5.4,0.77,7.09,5.6,null,null,null,null,null,null,13.4,0.8,7.1,4.5999999999999996]
[0,0,1,1,"2017-01-08",4003.7840277777777,1.01,7.09,4.8,0.85,7.09,5.6,null,null,null,null,null,null,14.2,0.7,7.1,4.8]
[0,0,1,1,"2017-01-09",4317.3166666666666,1.17,7.09,5,1.03,7.08,5,null,null,null,null,null,null,13,0.7,7.2,4.7]
[0,0,1,1,"2017-01-10",3821.2680555555557,1.47,7.17,4.8,0.36,7.16,4.9000000000000004,null,null,null,null,null,null,12.9,0.7,7.2,4.9000000000000004]
[0,0,1,1,"2017-01-11",4111.1034722222221,1.18,7.04,5.0999999999999996,0.82,7.1,5.9,null,null,null,null,null,null,13.3,0.8,7.2,4.8]
[0,0,1,1,"2017-01-12",4337.7791666666662,1.5,7.16,5.0999999999999996,0.9,7.16,4.7,null,null,null,null,null,null,13.5,0.78,7.2,4.7]
[0,0,1,1,"2017-01-13",4042.0034722222222,1.5,7.16,5,0.75,7.11,4.8,null,null,null,null,null,null,13,0.89,7.2,4.7]
[0,0,1,1,"2017-01-14",3733.1326388888888,1.6,7.14,5.0999999999999996,0.83,7.15,4.7,null,null,null,null,null,null,13,0.7,7.3,4.9000000000000004]
[0,0,1,1,"2017-01-15",3739.2430555555557,0.94,6.93,5.0999999999999996,0.82,7.05,4.7,null,null,null,null,null,null,12,0.7,7.1,5]
[0,0,1,1,"2017-01-16",3603.4812499999998,1.31,7.08,5.5,1.26,7.04,5.3,null,null,null,null,null,null,13.5,0.85,7.1,5.2]
[0,0,1,1,"2017-01-17",3260.036111111111,1.38,7.05,4.9000000000000004,0.88,7.07,5,null,null,null,null,null,null,11.8,0.79,7.1,4.5]
[0,0,1,1,"2017-01-18",3466.5430555555554,1.34,7.14,5.0999999999999996,0.93,7.1,5.0999999999999996,null,null,null,null,null,null,13,0.89,7.2,4.9000000000000004]
[0,0,1,1,"2017-01-19",3810.4916666666668,1.29,7.09,5.0999999999999996,0.99,7.1,5.0999999999999996,null,null,null,null,null,null,12.5,0.84,7.2,5.2]
[0,0,1,1,"2017-01-20",3611.1305555555555,1.1000000000000001,7.08,6.9,0.98,7,5.4,null,null,null,null,null,null,14.2,0.8,7.1,4.4000000000000004]
[0,0,1,1,"2017-01-21",3617.3048611111112,1.6,7.06,5.3,0.53,7.09,5.5,null,null,null,null,null,null,12.9,0.9,7.1,5.2]
[0,0,1,1,"2017-01-22",3808.3826388888888,1.45,7.1,5.9,1.04,7.11,5.8,null,null,null,null,null,null,11.9,0.87,7.1,5.2]
[0,0,1,1,"2017-01-23",3783.9513888888887,1.43,7.06,6,0.98,7.07,5.9,null,null,null,null,null,null,11.9,0.9,7.2,5.5]
[0,0,1,1,"2017-01-24",3483.5652777777777,1.24,7.17,5.7,0.9,7.16,5.4,null,null,null,null,null,null,12.5,0.9,7.2,5.4]
[0,0,1,1,"2017-01-25",3413.7541666666666,1.24,7.18,5.2,0.96,7.23,5.3,null,null,null,null,null,null,12.5,0.9,7.2,5.0999999999999996]
[0,0,1,1,"2017-01-26",3520.3979166666668,1.05,7.25,5.5,0.87,7.09,5.3,null,null,null,null,null,null,13.2,0.9,7.1,5.3]
[0,0,1,1,"2017-01-27",3542.2506944444444,1.1599999999999999,7.16,6.1,0.79,7.04,6.2,null,null,null,null,null,null,13.6,0.87,7.3,6]
[0,0,1,1,"2017-01-28",3506.2361111111113,1.17,7.05,6,0.9,7.02,6.1,null,null,null,null,null,null,14.2,0.9,7.2,6.4]
[0,0,1,1,"2017-01-29",3442.1125000000002,0.95,6.92,5.9,0.9,7,6,null,null,null,null,null,null,12.8,0.8,7.1,6]
[0,0,1,1,"2017-01-30",3596.7291666666665,1.08,7.13,6.4,0.85,7.13,6.4,null,null,null,null,null,null,13.2,0.86,7.2,6.1]
[0,0,1,1,"2017-01-31",3623.0895833333334,1.18,7.17,5.9,0.7,7.01,5.7,null,null,null,null,null,null,12.4,0.9,7.2,6.1]
["feb","feb",2,2,"2017-02-01",3619.4219061458152,1.62,7.26,5.8,1.2,7,6,null,null,null,null,null,null,11.3,1.7,7.1,5.4]
["feb","feb",2,2,"2017-02-02",4143.1265691404933,1.88,7.13,5.7,1.52,7.15,5.7,null,null,null,null,null,null,14.3,1.67,7.2,5.8]
["feb","feb",2,2,"2017-02-03",4134.0956158355057,1.8,7.06,6.4,1.19,7.08,5.9,null,null,null,null,null,null,13.6,1.82,7.1,6.8]
["feb","feb",2,2,"2017-02-04",3394.5612755668039,1.63,7.1,5.7,1.49,7.05,5.5,null,null,null,null,null,null,13.9,1.65,7.2,6.3]
["feb","feb",2,2,"2017-02-05",3814.2793284125141,1.72,7.07,6.8,1.24,7.09,7,null,null,null,null,null,null,13.6,1.1000000000000001,7.3,6.3]
["feb","feb",2,2,"2017-02-06",3449.3895330821088,1.4,7.12,6.4,1,7.12,6.8,null,null,null,null,null,null,13.9,1,7.1,6.9]
["feb","feb",2,2,"2017-02-07",3326.7904066213964,1.32,7.13,6.8,1.21,7.15,7.6,null,null,null,null,null,null,13.9,1.02,7.2,7.6]
["feb","feb",2,2,"2017-02-08",4267.0623297568318,1.1200000000000001,7.11,10.7,0.96,6.94,8.3000000000000007,null,null,null,null,null,null,13.9,0.8,7.2,8.5]
["feb","feb",2,2,"2017-02-09",4255.4973694014761,1.43,7.08,8.8000000000000007,1.1100000000000001,7.08,8.4,null,null,null,null,null,null,13,1,7.2,8.4]
["feb","feb",2,2,"2017-02-10",3327.1671088692751,1.19,7.15,8,0.8,7.04,8.1999999999999993,null,null,null,null,null,null,14.4,1.2,7.2,8.3000000000000007]
["feb","feb",2,2,"2017-02-11",3707.0647886117667,1.2,7.18,8.1999999999999993,0.8,7.08,8.1,null,null,null,null,null,null,14.5,1.2,7.2,8.1999999999999993]
["feb","feb",2,2,"2017-02-12",4253.9192240697257,1.32,7.12,9.1999999999999993,0.96,7.1,8.9,null,null,null,null,null,null,15.1,1.2,7.2,8.8000000000000007]
["feb","feb",2,2,"2017-02-13",4244.2446457170354,1.32,7.14,9.8000000000000007,0.92,7.06,9.1,null,null,null,null,null,null,14.3,1.04,7.1,9.1]
["feb","feb",2,2,"2017-02-14",3822.9018003953297,1.22,7.12,9.1,0.76,7.1,9.1999999999999993,null,null,null,null,null,null,14.7,1.1100000000000001,7.2,9.9]
["feb","feb",2,2,"2017-02-15",3959.599097909645,1.28,6.89,10.3,0.87,6.98,9.6,null,null,null,null,null,null,13.6,1.22,7.1,10.7]
["feb","feb",2,2,"2017-02-16",3268.0281124761354,1.42,7.11,9.8000000000000007,0.8,7.13,9.9,null,null,null,null,null,null,11.7,1.23,7.2,9.3000000000000007]
["feb","feb",2,2,"2017-02-17",3316.779720414424,1.2,7.06,10.1,0.92,7.09,10,null,null,null,null,null,null,13.4,1.3,7.1,9]
["feb","feb",2,2,"2017-02-18",4130.3934066148222,1.3,7.02,10.6,0.8,7.04,10.3,null,null,null,null,null,null,13.7,1.3,7.1,9.9]
["feb","feb",2,2,"2017-02-19",3963.5634820578025,1.31,7.07,10.1,0.88,7.06,10.3,null,null,null,null,null,null,10.1,0.8,7.2,8.9]
["feb","feb",2,2,"2017-02-20",3436.3377628929306,1.22,7.12,10.6,0.98,7.14,10.6,null,null,null,null,null,null,10.6,0.87,7.1,10.4]
["feb","feb",2,2,"2017-02-21",3622.2508119190088,0.82,7.14,10.8,0.81,7.18,10.7,null,null,null,null,null,null,13.7,0.8,7.2,10.4]
["feb","feb",2,2,"2017-02-22",3680.365047293868,1.39,7.14,11.9,1.05,7.07,11.1,null,null,null,null,null,null,12.4,0.6,7.1,10.8]
["feb","feb",2,2,"2017-02-23",4337.6958814041564,1.55,7.25,12.5,0.84,7.27,12.3,null,null,null,null,null,null,13,0.87,7.2,11.3]
["feb","feb",2,2,"2017-02-24",3283.6577769867663,1.2,7.12,10.8,0.94,7.05,10.9,null,null,null,null,null,null,11.6,0.97,7.1,11.4]
["feb","feb",2,2,"2017-02-25",4026.2637111137865,1.1200000000000001,7.05,10.1,0.99,7.08,9.9,null,null,null,null,null,null,9.6,0.8,7.1,11.2]
["feb","feb",2,2,"2017-02-26",4006.009802698979,0.75,7.04,11.8,0.55000000000000004,6.68,10.8,null,null,null,null,null,null,10,0.69,7.1,11.3]
["feb","feb",2,2,"2017-02-27",3594.7053042190209,1,7.13,11,0.73,7.14,10.9,null,null,null,null,null,null,14,0.9,7.1,10.9]
["feb","feb",2,2,"2017-02-28",4318.4408445550207,1.03,7.13,11.7,0.6,7.13,11.2,null,null,null,null,null,null,13.9,0.92,7.2,11]
[0,0,3,3,"2017-03-01",3627.9005199200537,1.08,7.06,12.1,0.79,7.05,12.1,null,null,null,null,null,null,14.5,1,7.1,11.9]
[0,0,3,3,"2017-03-02",3855.302170838389,1.28,7.08,13,0.79,7.08,12.9,null,null,null,null,null,null,13.3,0.86,7.1,12.4]
[0,0,3,3,"2017-03-03",4010.8984539197681,1.7,7.05,11.9,0.7,7.05,12,null,null,null,null,null,null,14.1,1,7.1,12.1]
[0,0,3,3,"2017-03-04",3430.9530761545479,1.3,7.14,12.3,0.6,7.05,13.7,null,null,null,null,null,null,14.5,0.96,7.1,13.6]
[0,0,3,3,"2017-03-05",3814.5050022914447,0.92,7.05,14.7,0.48,7.07,14.8,null,null,null,null,null,null,10.9,0.97,7.2,14]
[0,0,3,3,"2017-03-06",3733.0325583170679,1.4,6.9,14.7,0.7,6.99,14.5,null,null,null,null,null,null,10.8,1.02,7.1,14]
[0,{"$f":"IF(MONTH(E73)=2,\"feb\",)","v":0},{"$f":"MONTH(E73)","v":3},3,"2017-03-07",3941.9624771079102,0.64,7.13,13.7,0.87,7,13.7,null,null,null,null,null,null,11.2,0.89,7.2,12.6]
[0,0,3,3,"2017-03-08",4007.2024283483715,1.2,7.09,14.2,0.61,7.1,13.8,null,null,null,null,null,null,13.9,0.96,7.1,15.3]
[0,0,3,3,"2017-03-09",3434.301049584903,0.84,7.1,14.3,0.47,7.03,14.5,null,null,null,null,null,null,13.7,0.92,7.1,14.2]
[0,0,3,3,"2017-03-10",3617.790271779319,1.1000000000000001,7.1,15.4,0.38,7.08,15.2,null,null,null,null,null,null,12.3,0.97,7.1,14]
[0,0,3,3,"2017-03-11",4297.9292582036078,1.2,7.06,15,0.52,7.12,15,null,null,null,null,null,null,13,1,7.1,14.4]
[0,0,3,3,"2017-03-12",4198.6434228694779,1.2,7.08,15.1,0.78,7.09,15.1,null,null,null,null,null,null,11.9,0.99,7.1,14.5]
[0,0,3,3,"2017-03-13",3880.0382568136033,1.06,6.92,14.5,0.54,6.97,14.7,null,null,null,null,null,null,9.1999999999999993,1.05,7.1,14.5]
[0,0,3,3,"2017-03-14",4224.0780118126368,1.03,7.13,14.9,0.65,7.08,14.6,null,null,null,null,null,null,9,0.92,7.1,14.6]
[0,0,3,3,"2017-03-15",4171.0957460450054,0.88,6.97,15.8,0.47,6.99,15.7,null,null,null,null,null,null,12.6,0.98,7,14.6]
[0,0,3,3,"2017-03-16",3751.4245153879665,1.04,6.98,15.1,0.4,7.02,15.1,null,null,null,null,null,null,9.9,0.99,7.1,14.6]
[0,0,3,3,"2017-03-17",3744.619932440618,0.93,7.04,15.5,0.52,7.08,15.6,null,null,null,null,null,null,11.9,0.91,7.2,15.4]
[0,0,3,3,"2017-03-18",3934.0853668979221,0.7,7.1,15.2,0.49,7.14,15.2,null,null,null,null,null,null,11.5,0.9,7.2,15.8]
[0,0,3,3,"2017-03-19",3275.3192656299443,0.7,7.04,15.2,0.39,7.04,16.3,null,null,null,null,null,null,11.6,0.91,7.1,15.6]
[0,0,3,3,"2017-03-20",3968.5993186723895,0.57999999999999996,7.13,15.8,0.31,7.2,15.9,null,null,null,null,null,null,11.6,0.89,7.2,16.100000000000001]
[0,0,3,3,"2017-03-21",4276.6276573688037,0.57999999999999996,7.27,16.3,0.37,7.19,15.8,null,null,null,null,null,null,10.3,0.93,7.1,16.3]
[0,0,3,3,"2017-03-22",4226.1080215770162,0.48,7.12,15.7,0.3,7.1,16,null,null,null,null,null,null,12.9,0.97,7.1,16.100000000000001]
[0,0,3,3,"2017-03-23",3975.1776039035776,0.76,7.18,16.5,0.36,7.22,16.3,null,null,null,null,null,null,11.9,0.95,7.3,16]
[0,0,3,3,"2017-03-24",3461.7811397390556,0.72,7.12,16.899999999999999,0.3,7.09,16.899999999999999,null,null,null,null,null,null,13.9,1.1000000000000001,7.1,16]
[0,0,3,3,"2017-03-25",4202.5618195960596,0.86,7.11,16.899999999999999,0.3,7.1,17,null,null,null,null,null,null,14.4,1.05,7.1,15]
[0,0,3,3,"2017-03-26",3718.2337130244318,0.85,7.02,16.7,0.45,7.11,16.8,null,null,null,null,null,null,13.4,0.82,7.1,16.600000000000001]
[0,0,3,3,"2017-03-27",4021.0561675138242,0.26,6.97,16.7,0.09,6.98,16.899999999999999,null,null,null,null,null,null,13.6,0.94,7.1,17]
[0,0,3,3,"2017-03-28",3459.9809739554457,1.02,7.05,16.600000000000001,0.3,7.14,16.7,null,null,null,null,null,null,9.6999999999999993,1.02,7.1,16.8]
[0,0,3,3,"2017-03-29",3939.8436228299593,0.85,7.02,17.2,0.31,7.09,17,null,null,null,null,null,null,10.5,0.98,7.1,16.7]
[0,0,3,3,"2017-03-30",3428.9516841378172,1.35,7.04,16.899999999999999,0.76,7.06,16.899999999999999,null,null,null,null,null,null,10.6,1.01,7.1,16.100000000000001]
[0,0,3,3,"2017-03-31",3354.9187936610051,1.1000000000000001,7.09,17.2,0.39,7.09,17,null,null,null,null,null,null,10.8,1.03,7.1,16.600000000000001]
[0,0,4,4,"2017-04-01",4311.6499695049406,1.2,7.05,16.7,0.39,7.11,16.8,null,null,null,null,null,null,13.3,0.9,7.1,15.6]
[0,0,4,4,"2017-04-02",4224.1912849769215,1.1599999999999999,7.05,17.3,0.69,6.97,17.100000000000001,null,null,null,null,null,null,12.5,0.92,7.1,17]
[0,0,4,4,"2017-04-03",3877.2594952382742,0.86,7.17,17.2,0.56999999999999995,7.18,17.3,null,null,null,null,null,null,11.6,0.88,7.2,16.7]
[0,0,4,4,"2017-04-04",3914.1983468185817,0.98,7.13,16.3,0.53,7.05,16.600000000000001,null,null,null,null,null,null,11,0.87,7.1,17]
[0,0,4,4,"2017-04-05",4295.8149567967594,1.06,7.03,17.3,0.77,7.05,17.399999999999999,null,null,null,null,null,null,11,1,7.1,17]
[0,0,4,4,"2017-04-06",3531.7498208625134,0.84,7.2,17,0.56999999999999995,7.09,17.100000000000001,null,null,null,null,null,null,13.7,1,7.1,16.7]
[0,0,4,4,"2017-04-07",4141.6633328561966,0.65,7.05,16.5,0.38,7.01,16.7,null,null,null,null,null,null,11.9,0.97,7.1,16.8]
[0,0,4,4,"2017-04-08",3358.3588716395993,0.82,7.07,16.399999999999999,0.56999999999999995,7.03,16.399999999999999,null,null,null,null,null,null,10,0.89,7.1,17.2]
[0,0,4,4,"2017-04-09",3794.8615297681245,0.89,7.06,16.600000000000001,0.47,7.01,16.600000000000001,null,null,null,null,null,null,11.3,1,7.1,16.899999999999999]
[0,0,4,4,"2017-04-10",3621.0576656084127,0.9,7.02,17,0.52,7.08,17.2,null,null,null,null,null,null,14.2,0.88,7.1,16.600000000000001]
[0,0,4,4,"2017-04-11",3829.7808882308996,0.59,7.17,17.399999999999999,0.12,7.08,17.5,null,null,null,null,null,null,11.3,1,7.1,17.3]
[0,0,4,4,"2017-04-12",3900.8391691921966,1.1399999999999999,7.05,17.7,0.43,7,17.5,null,null,null,null,null,null,14.8,1,7.1,17.3]
[0,0,4,4,"2017-04-13",4266.9555177079128,0.65,6.95,18.3,0.32,7.1,18,null,null,null,null,null,null,12.2,0.71,7.1,18.100000000000001]
[0,0,4,4,"2017-04-14",3998.1985756050453,0.83,7.11,17.2,0.3,7.05,17,null,null,null,null,null,null,13.2,0.8,7.1,17.600000000000001]
[0,0,4,4,"2017-04-15",3646.838817719879,1.03,7.1,17.8,0.3,7.03,17.399999999999999,null,null,null,null,null,null,12.4,0.8,7.1,17.8]
[0,0,4,4,"2017-04-16",4253.4365271993302,1.05,7.04,17.600000000000001,0.27,7.04,17.7,null,null,null,null,null,null,11.5,0.71,7,17.399999999999999]
[0,0,4,4,"2017-04-17",3770.0226961019844,0.54,7.02,18.2,0.28999999999999998,7.03,18.8,null,null,null,null,null,null,12.7,0.72,7.1,18.100000000000001]
[0,0,4,4,"2017-04-18",4146.1724476172722,0.88,6.88,17.8,0.34,6.86,18,null,null,null,null,null,null,12.7,0.72,7.1,17.8]
[0,0,4,4,"2017-04-19",3545.2233806673739,1.25,7.05,17.5,0.43,6.97,17.899999999999999,null,null,null,null,null,null,11.3,0.68,7,17.600000000000001]
[0,0,4,4,"2017-04-20",3806.6082970435255,1,7,17.5,0.3,7.01,17.600000000000001,null,null,null,null,null,null,12.4,0.92,7.1,18]
[0,0,4,4,"2017-04-21",3609.3224054594743,0.8,7.03,18,0.49,7.05,18,null,null,null,null,null,null,13.9,1.1399999999999999,7.1,17.600000000000001]
[0,0,4,4,"2017-04-22",3913.5906281073699,0.9,7.03,17.7,0.3,7.05,17.899999999999999,null,null,null,null,null,null,12.6,1.17,7,17.399999999999999]
[0,0,4,4,"2017-04-23",3478.4215200908748,0.96,7.17,18,0.4,7.19,18.100000000000001,null,null,null,null,null,null,10.9,1.1000000000000001,7.1,17.7]
[0,0,4,4,"2017-04-24",4040.0436182231952,0.72,7.56,18,0.67,7.16,18.8,null,null,null,null,null,null,11.9,1.05,7.4,18.100000000000001]
[0,0,4,4,"2017-04-25",4225.1108474508828,1.07,7.42,18.100000000000001,0.39,7.38,19,null,null,null,null,null,null,11.5,1.2,7.4,18.5]
[0,0,4,4,"2017-04-26",3962.6453484697099,0.62,7.55,18.100000000000001,0.28999999999999998,7.48,18.5,null,null,null,null,null,null,10.199999999999999,1.22,7.4,18.3]
[0,0,4,4,"2017-04-27",3987.7953461035322,0.79,7.63,18.600000000000001,0.47,7.59,18.3,null,null,null,null,null,null,14,1.17,7.6,18.2]
[0,0,4,4,"2017-04-28",3452.3668661384759,0.68,7.5,18.2,0.32,7.48,18.3,null,null,null,null,null,null,12.1,1.17,7.5,18.8]
[0,0,4,4,"2017-04-29",3720.6781647770131,0.52,7.48,18.5,0.42,7.47,18.5,null,null,null,null,null,null,9.9,1.1299999999999999,7.5,18.8]
[0,0,4,4,"2017-04-30",3885.8082457236565,0.47,7.52,18.399999999999999,0.2,7.6,18.600000000000001,null,null,null,null,null,null,9.1999999999999993,1.2,7.5,18.899999999999999]
[0,0,5,5,"2017-05-01",4157.0742197375675,0.71,7.4,18.399999999999999,0.39,7.38,18.5,null,null,null,null,null,null,10.5,1.2,7.4,18.399999999999999]
[0,0,5,5,"2017-05-02",3809.1024050317183,0.41,7.46,19.3,0.22,7.48,19.3,null,null,null,null,null,null,13.4,1.1100000000000001,7.4,18.899999999999999]
[0,0,5,5,"2017-05-03",3279.7532192460017,0.77,7.49,18.899999999999999,0.48,7.43,18.899999999999999,null,null,null,null,null,null,14.1,1.24,7.4,18.7]
[0,0,5,5,"2017-05-04",3345.5769449933509,0.6,7.43,19.5,0.47,7.39,19.5,null,null,null,null,null,null,12.5,1.24,7.4,19]
[0,0,5,5,"2017-05-05",3831.6020236326067,0.62,7.57,19.7,0.4,7.55,19.5,null,null,null,null,null,null,14.9,1.18,7.4,19.5]
[0,0,5,5,"2017-05-06",4068.4406267727545,0.98,7.57,19.899999999999999,0.3,7.54,20.2,null,null,null,null,null,null,11.8,1.1499999999999999,7.4,20.2]
[0,0,5,5,"2017-05-07",3298.3389784215437,0.7,7.46,20.399999999999999,0.2,7.51,20.3,null,null,null,null,null,null,9.6,1.1399999999999999,7.4,20.100000000000001]
[0,0,5,5,"2017-05-08",4111.1071689989058,1.1299999999999999,7.45,20.399999999999999,0.57999999999999996,7.42,20.6,null,null,null,null,null,null,11.2,1.24,7.4,20.399999999999999]
[0,0,5,5,"2017-05-09",3650.1397512286935,0.54,7.41,20.8,0.28999999999999998,7.41,20.8,null,null,null,null,null,null,11.6,1.2,7.4,21.1]
[0,{"$f":"IF(MONTH(E137)=2,\"feb\",)","v":0},{"$f":"MONTH(E137)","v":5},5,"2017-05-10",3575.9425407276594,0.26,7.57,22,0.2,7.4,21.8,null,null,null,null,null,null,13,0.93,7.5,21.3]
[0,0,5,5,"2017-05-11",4211.1432279143819,0.63,7.31,21.4,0.17,7.3,21.5,null,null,null,null,null,null,9.6,1.74,7.4,21.2]
[0,0,5,5,"2017-05-12",3533.8628190909621,0.98899999999999999,7.5,21.4,0.19,7.49,21.5,null,null,null,null,null,null,13,1.85,7.4,21.4]
[0,0,5,5,"2017-05-13",4174.1222630292541,0.31,7.4,21.4,0.46,7.43,21.5,null,null,null,null,null,null,9.3000000000000007,1.93,7.4,22]
[0,0,5,5,"2017-05-14",3916.8490570468848,0.52,7.54,22.5,0.2,7.52,22.6,null,null,null,null,null,null,9.3000000000000007,1.76,7.5,21.6]
[0,0,5,5,"2017-05-15",4344.3590906539821,0.65,7.27,22.4,0.4,7.27,22.2,null,null,null,null,null,null,11.6,1.62,7.4,22.4]
[0,0,5,5,"2017-05-16",3357.458797654197,0.72,7.33,21.9,0.32,7.3,22.3,null,null,null,null,null,null,10.1,1.7,7.4,22.3]
[0,0,5,5,"2017-05-17",3274.6477051492138,0.52,7.51,22.7,0.14000000000000001,7.55,22.8,null,null,null,null,null,null,14.9,1.27,7.6,22.7]
[0,0,5,5,"2017-05-18",3775.2629854027077,0.33,7.36,22.8,0.21,7.36,22.9,null,null,null,null,null,null,12.6,1.47,7.4,22.8]
[0,0,5,5,"2017-05-19",3371.3729005044975,0.4,7.32,22.3,0.19,7.48,23,null,null,null,null,null,null,14.9,1.44,7.4,22.6]
[0,0,5,5,"2017-05-20",4281.0008108548118,0.3,7.37,22.5,0.37,7.43,22.9,null,null,null,null,null,null,11.1,1.5,7.4,23.1]
[0,0,5,5,"2017-05-21",3872.6308408126793,0.48,7.34,23.4,0.27,7.35,23.5,null,null,null,null,null,null,13.1,1.46,7.4,23.3]
[0,0,5,5,"2017-05-22",3587.3083369076576,0.56000000000000005,7.38,24.6,0.39,7.5,24.2,null,null,null,null,null,null,11,1.2,7.4,24.3]
[0,0,5,5,"2017-05-23",3766.8443314621186,0.27,7.42,24.6,0.13,7.42,24.4,null,null,null,null,null,null,11.3,1.2,7.4,24]
[0,0,5,5,"2017-05-24",3763.9168743770815,0.68,7.46,23.5,0.28999999999999998,7.43,23.9,null,null,null,null,null,null,11.7,1.2,7.5,23.9]
[0,0,5,5,"2017-05-25",3409.203934788598,0.54,7.44,24,0.18,7.43,24.2,null,null,null,null,null,null,12.3,1.2,7.5,24.4]
[0,0,5,5,"2017-05-26",4188.5357325824216,0.57999999999999996,7.43,24.4,0.28999999999999998,7.43,24.3,null,null,null,null,null,null,12.6,1.1599999999999999,7.5,24.5]
[0,0,5,5,"2017-05-27",4195.6019350799243,0.45,7.41,24.9,0.2,7.43,25,null,null,null,null,null,null,13.9,1.1499999999999999,7.4,25]
[0,0,5,5,"2017-05-28",3293.5759926165292,0.68,7.35,25,0.28000000000000003,7.46,24.4,null,null,null,null,null,null,11.8,1.2,7.5,24.4]
[0,0,5,5,"2017-05-29",3841.4307300224659,0.28999999999999998,7.33,25.8,0.08,7.36,25.7,null,null,null,null,null,null,12.6,1.17,7.4,25.5]
[0,0,5,5,"2017-05-30",4166.9397465106777,0.54,7.49,25,0.36,7.48,25.9,null,null,null,null,null,null,13.9,1.19,7.7,25.8]
[0,0,5,5,"2017-05-31",3876.625160275174,0.99,7.58,25.9,0.36,7.48,26.2,null,null,null,null,null,null,11.7,1.1499999999999999,7.6,26.3]
[0,0,6,6,"2017-06-01",3316.6542729574076,0.73,7.42,25.8,0.48,7.35,26.5,null,null,null,null,null,null,10.5,1.06,7.5,26.6]
[0,0,6,6,"2017-06-02",3498.9168414294745,0.3,7.42,25.6,0.41,7.39,26,null,null,null,null,null,null,10.7,1.1200000000000001,7.4,25.8]
[0,0,6,6,"2017-06-03",3716.5362422759968,0.2,7.39,25.7,0.21,7.39,25.6,null,null,null,null,null,null,10.9,1.1499999999999999,7.4,25.6]
[0,0,6,6,"2017-06-04",3784.3213080881105,0.4,7.43,25.2,0.24,7.36,25.3,null,null,null,null,null,null,13.4,1.29,7.4,25.2]
[0,0,6,6,"2017-06-05",3841.6689342054169,1.51,7.36,27.6,0.62,7.06,26.7,null,null,null,null,null,null,9.6,1.1299999999999999,7.5,25.9]
[0,0,6,6,"2017-06-06",3765.2138915305077,0.74,7.32,25.6,0.34,7.39,26.3,null,null,null,null,null,null,11.4,1.1200000000000001,7.4,25.8]
[0,0,6,6,"2017-06-07",3878.0469862199093,0.78,7.48,25.8,0.36,7.41,26.3,null,null,null,null,null,null,11,1.1499999999999999,7.6,26.2]
[0,0,6,6,"2017-06-08",3479.7065134844256,0.85,7.75,23.6,0.15,7.4,26.4,null,null,null,null,null,null,14.5,1.07,7.6,26.2]
[0,0,6,6,"2017-06-09",3826.8579559088735,0.18,7.48,25.8,0.32,7.53,26,null,null,null,null,null,null,11.8,1.06,7.5,26.4]
[0,0,6,6,"2017-06-10",3290.3637711697224,0.85,7.69,26,0.39,7.54,26.1,null,null,null,null,null,null,10.6,1.18,7.6,26.3]
[0,0,6,6,"2017-06-11",3723.340714237273,1.1120000000000001,7.54,26.5,0.39,7.44,26.4,null,null,null,null,null,null,10.9,1.21,7.5,26.4]
[0,0,6,6,"2017-06-12",3885.8652384708444,1.35,7.44,26.5,0.34,7.46,26.6,null,null,null,null,null,null,11.9,1.2,7.5,26.6]
[0,0,6,6,"2017-06-13",4013.0336504596216,0.76,7.36,26.9,0.13,7.41,26.9,null,null,null,null,null,null,12.6,1.18,7.4,26.2]
[0,0,6,6,"2017-06-14",3593.913253881602,1.38,7.4,26.5,0.63,7.42,26.6,null,null,null,null,null,null,12.6,1.3,7.4,26.5]
[0,0,6,6,"2017-06-15",4094.4291633580383,1.3,7.57,27,0.51,7.52,27,null,null,null,null,null,null,10.4,1.5,7.5,26.9]
[0,0,6,6,"2017-06-16",3446.1405991494144,0.7,7.41,26.9,0.4,7.54,26.8,null,null,null,null,null,null,12.9,1.4,7.5,26.9]
[0,0,6,6,"2017-06-17",3304.1928195129067,1.5,7.41,26.8,0.4,7.54,27.1,null,null,null,null,null,null,13.6,1.4,7.4,26.8]
[0,0,6,6,"2017-06-18",4231.8316668088128,1.0900000000000001,7.52,26.7,0.57999999999999996,7.48,26.8,null,null,null,null,null,null,14.8,1.39,7.5,27.8]
[0,0,6,6,"2017-06-19",4139.6806620123816,0.96,7.59,27.6,0.54,7.52,27.4,null,null,null,null,null,null,10.7,1.33,7.6,27]
[0,0,6,6,"2017-06-20",3312.7367802144477,0.66,7.52,26.8,0.21,7.5,27,null,null,null,null,null,null,15.1,1.3,7.6,27.4]
[0,0,6,6,"2017-06-21",3435.4077810376953,0.3,7.45,27.3,0.34,7.47,27.6,null,null,null,null,null,null,14.8,1.33,7.5,27.5]
[0,0,6,6,"2017-06-22",3281.0434019289951,0.48,7.59,27.8,0.23,7.54,27.8,null,null,null,null,null,null,12.5,1.58,7.5,27.3]
[0,0,6,6,"2017-06-23",4005.0955940259105,0.28999999999999998,7.42,27.5,0.15,7.44,27.6,null,null,null,null,null,null,12.2,1.68,7.4,27.4]
[0,0,6,6,"2017-06-24",3312.4193526167705,0.81,7.29,27.1,0.09,7.39,22.5,null,null,null,null,null,null,16.100000000000001,1.73,7.5,27.4]
[0,0,6,6,"2017-06-25",3994.0154001931901,0.9,7.36,27.8,0.18,7.41,28.1,null,null,null,null,null,null,13.3,1.62,7.4,27.8]
[0,0,6,6,"2017-06-26",3950.3414608197772,1.36,7.55,27.5,0.3,7.5,28,null,null,null,null,null,null,12.6,1.76,7.4,27.8]
[0,0,6,6,"2017-06-27",3912.6004552839072,1.05,7.5,27.4,0.28999999999999998,7.43,28.1,null,null,null,null,null,null,13.5,1.62,7.4,28.1]
[0,0,6,6,"2017-06-28",3931.7783042306728,1.05,7.54,27,0.27,7.32,28.1,null,null,null,null,null,null,13.5,1.65,7.4,27.9]
[0,0,6,6,"2017-06-29",3919.0089082376953,1.44,7.49,28.4,0.33,7.44,28.2,null,null,null,null,null,null,12,1.62,7.4,27.5]
[0,0,6,6,"2017-06-30",3521.5481915304626,1.02,7.47,27.4,0.56000000000000005,7.4,28.2,null,null,null,null,null,null,14,1.64,7.4,27.6]
[0,0,7,7,"2017-07-01",3288.8164762416122,1.04,7.43,28,0.2,7.41,27.8,null,null,null,null,null,null,12,0.66,7.4,27.9]
[0,0,7,7,"2017-07-02",4096.5539612630337,3.2,7.42,27.6,1.4410000000000001,7.41,27.5,null,null,null,null,null,null,9.4,0.86,7.4,27.7]
[0,0,7,7,"2017-07-03",3798.0521967109139,1.26,7.38,27.9,0.55000000000000004,7.42,27.8,null,null,null,null,null,null,13.2,1.56,7.4,27.9]
[0,0,7,7,"2017-07-04",3321.1919703758876,1.24,7.37,27.4,0.56999999999999995,7.39,27.9,null,null,null,null,null,null,10.8,1.66,7.4,27.7]
[0,0,7,7,"2017-07-05",3682.8204164435415,0.5,7.92,27.7,0.18,7.36,27.9,null,null,null,null,null,null,13.7,1.68,7.4,27.6]
[0,0,7,7,"2017-07-06",4137.7679772377378,1.5,7.37,27.2,0.59,7.33,27.6,null,null,null,null,null,null,11.4,1.7,7.4,27.2]
[0,0,7,7,"2017-07-07",4244.2956766897087,0.59,7.47,26.5,0.22,7.44,27.5,null,null,null,null,null,null,12.1,1.69,7.4,27.2]
[0,0,7,7,"2017-07-08",4074.8258757160584,0.51,7.46,26.9,0.23,7.47,27.8,null,null,null,null,null,null,12.6,1.7,7.4,27.6]
[0,0,7,7,"2017-07-09",3558.2455729047815,0.74,7.34,27,0.59,7.35,27,null,null,null,null,null,null,11.7,1.61,7.3,27.7]
[0,0,7,7,"2017-07-10",3984.1604254649487,0.73,7.49,28.2,0.41,7.51,28.1,null,null,null,null,null,null,13.4,1.51,7.4,27.8]
[0,0,7,7,"2017-07-11",3282.0470904288113,1.06,7.58,27.9,0.21,7.42,27.9,null,null,null,null,null,null,13.3,1.7,7.4,27.9]
[0,0,7,7,"2017-07-12",4174.8731950465562,1.1200000000000001,7.34,27.6,0.53,7.46,27.6,null,null,null,null,null,null,13.9,1.53,7.4,27.6]
[0,{"$f":"IF(MONTH(E201)=2,\"feb\",)","v":0},{"$f":"MONTH(E201)","v":7},7,"2017-07-13",3899.0927817050742,1.1299999999999999,7.34,27.5,0.53,7.35,27.9,null,null,null,null,null,null,14.3,1.7,7.4,27.8]
[0,0,7,7,"2017-07-14",3526.5530742053566,0.9,7.31,27.5,0.27,7.36,27.8,null,null,null,null,null,null,12.9,1.7,7.3,28]
[0,0,7,7,"2017-07-15",3946.936957121874,0.4,7.38,27.5,0.09,7.33,27.6,null,null,null,null,null,null,16.100000000000001,1.7,7.4,27.9]
[0,0,7,7,"2017-07-16",3924.5433480569241,1.1100000000000001,7.47,28.1,0.56000000000000005,7.45,28.1,null,null,null,null,null,null,13.2,1.63,7.4,27.8]
[0,0,7,7,"2017-07-17",4062.375440282116,1.08,7.54,28.2,0.52,7.52,28.1,null,null,null,null,null,null,15.2,1.6,7.6,28.5]
[0,0,7,7,"2017-07-18",3909.1867313519388,0.81,7.39,28.2,0.38,7.39,28.1,null,null,null,null,null,null,9.3000000000000007,1.62,7.4,28]
[0,0,7,7,"2017-07-19",4151.5343380145778,0.75,7.41,28.2,0.36,7.44,28.1,null,null,null,null,null,null,14.6,1.57,7.4,28.2]
[0,0,7,7,"2017-07-20",3901.6816961694976,1.04,7.49,28.2,0.49,7.47,28.1,null,null,null,null,null,null,11.7,1.72,7.4,27.9]
[0,0,7,7,"2017-07-21",3665.5797294926142,1.06,7.45,26.6,0.23,7.43,27.7,null,null,null,null,null,null,14.4,1.65,7.4,27.6]
[0,0,7,7,"2017-07-22",3794.4346915642459,0.92,7.42,26.9,0.4,7.31,27.7,null,null,null,null,null,null,13.5,1.7,7.3,27.2]
[0,0,7,7,"2017-07-23",3752.9409519297114,0.9,7.45,26.7,0.4,7.43,27.3,null,null,null,null,null,null,14.5,1.6,7.4,27.1]
[0,0,7,7,"2017-07-24",3652.792379371157,0.7,7.39,27.4,0.3,7.32,27.6,null,null,null,null,null,null,12.9,1.7,7.4,27.1]
[0,0,7,7,"2017-07-25",3739.7317659500391,1,7.35,26.7,0.27,7.36,26.9,null,null,null,null,null,null,12.5,1.6,7.4,27]
[0,0,7,7,"2017-07-26",3766.3610915041763,0.53,7.48,26.3,0.18,7.38,26.6,null,null,null,null,null,null,14.7,1.67,7.4,26.8]
[0,0,7,7,"2017-07-27",3425.4646641276272,1.1599999999999999,7.5,25.3,0.47,7.44,26.4,null,null,null,null,null,null,13.6,1.36,7.4,26.2]
[0,0,7,7,"2017-07-28",4020.621212271983,0.68,7.49,26.1,0.3,7.31,26.4,null,null,null,null,null,null,14.1,1.59,7.3,26.1]
[0,0,7,7,"2017-07-29",4084.3598557331761,1.02,7.39,26.5,0.3,7.48,26.7,null,null,null,null,null,null,13,1.54,7.4,26.1]
[0,0,7,7,"2017-07-30",3302.1144492701114,1.07,7.4,26.2,0.32,7.44,26.1,null,null,null,null,null,null,10.9,1.67,7.4,26.1]
[0,0,7,7,"2017-07-31",4227.6586120911952,1.32,7.45,25.8,0.46,7.42,25.9,null,null,null,null,null,null,11.8,1.73,7.4,25.8]
[0,0,8,8,"2017-08-01",3841.6593322937179,1.3,7.36,25.6,0.21,7.32,26.4,null,null,null,null,null,null,10.7,0.5,7.4,25.9]
[0,0,8,8,"2017-08-02",3273.0982188323997,0.82,7.56,26.6,0.26,7.47,26.6,null,null,null,null,null,null,9.6999999999999993,1.77,7.4,26.4]
[0,0,8,8,"2017-08-03",3620.7721065776364,0.42,7.32,26.3,0.15,7.29,26.2,null,null,null,null,null,null,14.6,1.79,7.3,26.5]
[0,0,8,8,"2017-08-04",3267.7113716238223,0.8,7.35,25.5,0.33,7.35,25.7,null,null,null,null,null,null,16.2,1.79,7.3,26.5]
[0,0,8,8,"2017-08-05",3299.4072344206843,0.7,7.34,24.7,0.11,7.31,25.2,null,null,null,null,null,null,15.6,1.75,7.3,25.3]
[0,0,8,8,"2017-08-06",3306.5607336429575,0.8,7.43,24.7,0.21,7.3,24.7,null,null,null,null,null,null,13.7,1.6,7.4,24.8]
[0,0,8,8,"2017-08-07",3461.3901999926329,0.78,7.36,24.7,0.3,7.37,24.4,null,null,null,null,null,null,10.9,1.63,7.4,24.9]
[0,0,8,8,"2017-08-08",3904.1327918842799,1.25,7.52,24.7,0.72,7.42,24.5,null,null,null,null,null,null,13.7,1.4,7.4,24.9]
[0,0,8,8,"2017-08-09",3616.0588864722258,1.02,7.52,24.5,0.3,7.34,24.5,null,null,null,null,null,null,12.4,1.65,7.3,24.4]
[0,0,8,8,"2017-08-10",4141.3342195097457,1.1100000000000001,7.28,23.8,0.34,7.29,24.5,null,null,null,null,null,null,12.6,1.65,7.4,24.1]
[0,0,8,8,"2017-08-11",4081.7313991252345,0.59,7.32,23.8,0.34,7.34,24.1,null,null,null,null,null,null,11.7,1.78,7.3,24]
[0,0,8,8,"2017-08-12",3658.6332427632751,0.53,7.42,23.2,0.09,7.41,23.7,null,null,null,null,null,null,11.3,1.64,7.4,24]
[0,0,8,8,"2017-08-13",3780.8588098650139,1.17,7.39,24.4,0.52,7.34,24.3,null,null,null,null,null,null,12.5,1.6,7.3,23.9]
[0,0,8,8,"2017-08-14",3398.5005030253405,1.21,7.42,23.5,0.13,7.36,23.4,null,null,null,null,null,null,15.5,1.72,7.3,23.8]
[0,0,8,8,"2017-08-15",4342.5709620176549,1.17,7.42,23.6,0.45,7.37,23.4,null,null,null,null,null,null,15,1.8,7.4,23.8]
[0,0,8,8,"2017-08-16",4322.8598677521886,1.1200000000000001,7.48,23.5,0.73,7.37,23.4,null,null,null,null,null,null,14.3,1.6,7.4,23.8]
[0,0,8,8,"2017-08-17",4267.3679261614143,1.18,7.35,23.9,0.47,7.34,23.9,null,null,null,null,null,null,13.5,1.79,7.4,23.9]
[0,0,8,8,"2017-08-18",3932.026166980856,1.07,7.33,23.4,0.2,7.33,23.7,null,null,null,null,null,null,11.5,1.69,7.4,23.7]
[0,0,8,8,"2017-08-19",3796.7527291031497,0.78,7.29,23.7,0.3,7.34,23.6,null,null,null,null,null,null,12.6,1.74,7.3,23.8]
[0,0,8,8,"2017-08-20",3808.5809823453942,0.23,7.39,23.8,0.08,7.26,23.6,null,null,null,null,null,null,14.9,1.67,7.4,23.9]
[0,0,8,8,"2017-08-21",3299.22572202826,1.48,7.44,23.7,0.25,7.37,23.6,null,null,null,null,null,null,14.5,1.73,7.4,23.8]
[0,0,8,8,"2017-08-22",3443.9273243092507,0.9,7.38,23.8,0.35,7.41,24,null,null,null,null,null,null,13.3,1.81,7.4,23.5]
[0,0,8,8,"2017-08-23",3496.5126322662327,0.6,7.45,23.7,0.03,7.44,24.2,null,null,null,null,null,null,14,1.76,7.4,24.5]
[0,0,8,8,"2017-08-24",4123.4467759183062,1,7.5,23.8,0.4,7.37,24.2,null,null,null,null,null,null,12.3,1.69,7.4,24.2]
[0,0,8,8,"2017-08-25",3621.3924251088561,0.2,7.35,22.1,0.18,7.41,22.3,null,null,null,null,null,null,16.5,1.8,7.4,22.6]
[0,0,8,8,"2017-08-26",4172.5013851455715,0.2,7.53,22.5,0.32,7.41,22.5,null,null,null,null,null,null,16.2,1.78,7.4,23.7]
[0,0,8,8,"2017-08-27",3302.9403145193155,0.77,7.43,23.1,0.56999999999999995,7.37,22.9,null,null,null,null,null,null,13.5,1.7,7.4,23.4]
[0,0,8,8,"2017-08-28",3587.6192979501179,0.55000000000000004,7.47,22.7,0.32,7.39,23,null,null,null,null,null,null,14.4,1.64,7.4,22.5]
[0,0,8,8,"2017-08-29",3443.4248728013813,1.1399999999999999,7.46,22,0.37,7.39,22.1,null,null,null,null,null,null,11,1.69,7.4,22.1]
[0,0,8,8,"2017-08-30",3554.3872311923674,1.06,7.46,21.8,0.42,7.39,21.9,null,null,null,null,null,null,15.3,1.64,7.4,21.9]
[0,0,8,8,"2017-08-31",4031.7456672268868,1.19,7.31,21.8,0.62,7.27,22.2,null,null,null,null,null,null,15.3,1.6,7.3,22]
[0,0,9,9,"2017-09-01",3638.6960442332784,1.1499999999999999,7.38,21.3,0.42,7.39,21.4,null,null,null,null,null,null,14.5,1.7,7.3,21.4]
[0,0,9,9,"2017-09-02",4074.4223194962065,1.33,7.42,20.5,0.41,7.4,20.8,null,null,null,null,null,null,14.8,1.7,7.3,20.8]
[0,0,9,9,"2017-09-03",3821.539739882895,0.97,7.47,20.2,0.54,7.39,20.3,null,null,null,null,null,null,14.7,1.58,7.3,20.100000000000001]
[0,0,9,9,"2017-09-04",3530.9449852410808,0.41,7.28,19.2,0.09,7.25,19.3,null,null,null,null,null,null,15.5,1.69,7.3,19.399999999999999]
[0,0,9,9,"2017-09-05",3703.8674882411065,1.37,7.52,18.899999999999999,0.37,7.44,19.100000000000001,null,null,null,null,null,null,13.6,1.19,7.4,19.2]
[0,0,9,9,"2017-09-06",4296.3861512895401,1.06,7.29,19.2,0.48,7.29,19.100000000000001,null,null,null,null,null,null,14.9,1.75,7.3,18.7]
[0,0,9,9,"2017-09-07",4188.1254975095535,1.23,7.5,18.600000000000001,0.56999999999999995,7.49,18.600000000000001,null,null,null,null,null,null,12.5,1.71,7.4,18.600000000000001]
[0,0,9,9,"2017-09-08",3510.5144077069208,0.94,7.29,18.899999999999999,0.44,7.38,18.8,null,null,null,null,null,null,12.7,1.69,7.3,18.7]
[0,0,9,9,"2017-09-09",3842.2944096638635,0.94,7.47,19.2,0.48,7.39,19.100000000000001,null,null,null,null,null,null,12.8,1.67,7.4,18.7]
[0,0,9,9,"2017-09-10",3559.8749773311142,1.2,7.43,19.100000000000001,0.46,7.43,18.899999999999999,null,null,null,null,null,null,15.7,1.77,7.4,18.600000000000001]
[0,0,9,9,"2017-09-11",3370.5287124042179,0.51,7.49,18.899999999999999,0.45,7.32,19,null,null,null,null,null,null,10.9,1.84,7.3,18.8]
[0,0,9,9,"2017-09-12",3385.3444053732287,0.51,7.49,18.8,0.24,7.39,19,null,null,null,null,null,null,13.4,1.68,7.4,19.100000000000001]
[0,0,9,9,"2017-09-13",3571.7573707916031,1,7.46,18.5,0.4,7.43,18.7,null,null,null,null,null,null,13,1.7,7.4,18.8]
[0,0,9,9,"2017-09-14",3605.4184396674223,0.9,7.6,18.8,0.68,7.43,18.899999999999999,null,null,null,null,null,null,13.9,1.8,7.4,18.7]
[0,{"$f":"IF(MONTH(E265)=2,\"feb\",)","v":0},{"$f":"MONTH(E265)","v":9},9,"2017-09-15",3473.3652317749111,1.1000000000000001,7.4,18.399999999999999,0.31,7.45,18.399999999999999,null,null,null,null,null,null,15.6,1.8,7.4,18.100000000000001]
[0,0,9,9,"2017-09-16",3443.3998491687566,0.9,7.38,17.399999999999999,0.28999999999999998,7.46,17.5,null,null,null,null,null,null,13.8,1.7,7.4,17.600000000000001]
[0,0,9,9,"2017-09-17",3302.0445320507488,0.96,7.5,17.600000000000001,0.54,7.35,17.600000000000001,null,null,null,null,null,null,12.7,1.7,7.4,18]
[0,0,9,9,"2017-09-18",3371.5144282471892,1.1200000000000001,7.42,18,0.28999999999999998,7.3,18.100000000000001,null,null,null,null,null,null,16.3,1.66,7.4,18.100000000000001]
[0,0,9,9,"2017-09-19",3650.6704120412237,1.21,7.49,17.5,0.54,7.45,17.7,null,null,null,null,null,null,13.8,1.7,7.4,17.600000000000001]
[0,0,9,9,"2017-09-20",3841.8116835830456,0.94,7.29,17.7,0.51,7.29,17.7,null,null,null,null,null,null,14.7,1.6,7.3,17.7]
[0,0,9,9,"2017-09-21",4056.9917725730188,0.79,7.52,17.3,0.33,7.44,17.2,null,null,null,null,null,null,13.7,1.63,7.5,17.399999999999999]
[0,0,9,9,"2017-09-22",4298.9749768539832,0.57999999999999996,7.4,16.600000000000001,0.16,7.45,16.600000000000001,null,null,null,null,null,null,14.5,1.62,7.4,17.100000000000001]
[0,0,9,9,"2017-09-23",3262.3261450788982,0.98,7.4,17.3,0.35,7.49,16.7,null,null,null,null,null,null,11.1,1.68,7.4,17.3]
[0,0,9,9,"2017-09-24",3647.282731070758,0.88,7.59,17,0.41,7.56,17,null,null,null,null,null,null,14,1.78,7.4,17.100000000000001]
[0,0,9,9,"2017-09-25",3407.0479377371971,0.78,7.39,17.2,0.61,7.36,17.2,null,null,null,null,null,null,13.6,1.7,7.4,16.899999999999999]
[0,0,9,9,"2017-09-26",3914.2379188749032,0.82,7.47,17.2,0.32,7.39,17.100000000000001,null,null,null,null,null,null,12.9,1.64,7.4,16.8]
[0,0,9,9,"2017-09-27",3512.7489327810522,0.88,7.45,17.100000000000001,0.4,7.39,17,null,null,null,null,null,null,14.3,1.71,7.4,16.899999999999999]
[0,0,9,9,"2017-09-28",3329.4072711838317,1.02,7.46,16.2,0.48,7.43,16.600000000000001,null,null,null,null,null,null,12.8,1.1299999999999999,7.4,16.600000000000001]
[0,0,9,9,"2017-09-29",3674.7741421393289,0.72,7.47,16.600000000000001,0.13,7.39,16.7,null,null,null,null,null,null,13,1.23,7.4,16]
[0,0,9,9,"2017-09-30",3548.0734791928567,0.78,7.31,15.9,0.4,7.32,16,null,null,null,null,null,null,13.8,1.47,7.4,15.7]
[0,0,10,10,"2017-10-01",3749.9405368624493,0.91,7.37,15.8,0.4,7.42,16.2,null,null,null,null,null,null,15.1,1.38,7.4,15.7]
[0,0,10,10,"2017-10-02",4025.1705064690614,0.77,7.57,15.5,0.43,7.37,15.6,null,null,null,null,null,null,12.6,1.32,7.4,15.5]
[0,0,10,10,"2017-10-03",3877.6476992358339,0.9,7.47,15.4,0.22,7.43,15.3,null,null,null,null,null,null,15.3,1.19,7.4,16.100000000000001]
[0,0,10,10,"2017-10-04",3969.969517741155,0.31,7.46,14.7,0.14000000000000001,7.43,15.2,null,null,null,null,null,null,14.7,1.17,7.4,14.4]
[0,0,10,10,"2017-10-05",3595.5043503741986,0.4,7.47,14.8,0.28999999999999998,7.42,14.9,null,null,null,null,null,null,14,1.1000000000000001,7.4,15]
[0,0,10,10,"2017-10-06",3668.0490518105848,0.4,7.5,14.5,0.28999999999999998,7.47,14.3,null,null,null,null,null,null,14,1.1499999999999999,7.4,14]
[0,0,10,10,"2017-10-07",4219.7183396263245,0.1,7.44,13.4,0.25,7.43,13.4,null,null,null,null,null,null,12.1,1.1299999999999999,7.4,12.9]
[0,0,10,10,"2017-10-08",3343.05459601759,0.76,7.47,13.1,0.28999999999999998,7.39,13,null,null,null,null,null,null,14.3,1.21,7.4,12.8]
[0,0,10,10,"2017-10-09",3512.3863617470793,0.74,7.51,12.9,0.41,7.42,12.9,null,null,null,null,null,null,13.2,1.06,7.4,12.8]
[0,0,10,10,"2017-10-10",3781.0391062659278,0.67,7.47,13.1,0.37,7.41,13,null,null,null,null,null,null,12.2,1.0900000000000001,7.4,13]
[0,0,10,10,"2017-10-11",3281.8943323159692,0.64,7.44,12.7,0.24,7.4,12.9,null,null,null,null,null,null,11,1.2,7.4,13]
[0,0,10,10,"2017-10-12",3811.2001101789228,0.69,7.49,13.1,0.44,7.41,13,null,null,null,null,null,null,10.9,1.2,7.5,12.8]
[0,0,10,10,"2017-10-13",3964.6521763100122,0.46,7.44,13.1,0.28000000000000003,7.52,12.6,null,null,null,null,null,null,10.5,1.36,7.5,13.1]
[0,0,10,10,"2017-10-14",3363.8317806807236,0.59,7.72,12.9,0.34,7.34,12.7,null,null,null,null,null,null,10.5,1.34,8,13.3]
[0,0,10,10,"2017-10-15",3498.8034291878366,0.48,7.46,12.9,0.31,7.39,12.8,null,null,null,null,null,null,10.5,1.2,7.5,12.8]
[0,0,10,10,"2017-10-16",3473.2878356607898,0.54,7.39,12.8,0.36,7.32,12.8,null,null,null,null,null,null,13.1,1.3,7.4,12.5]
[0,0,10,10,"2017-10-17",3709.8090533507934,0.36,7.43,12.4,0.16,7.41,12.3,null,null,null,null,null,null,12.2,1.35,7.5,12.3]
[0,0,10,10,"2017-10-18",3819.0517241552593,0.68,7.37,11.9,0.28999999999999998,7.34,11.8,null,null,null,null,null,null,9.5,1.24,7.4,11.9]
[0,0,10,10,"2017-10-19",3469.5726306481442,0.8,7.2,12.7,0.36,7.22,12.1,null,null,null,null,null,null,13.2,1.4,7.4,12]
[0,0,10,10,"2017-10-20",3679.3925266874812,0.62,7.41,11.9,0.28000000000000003,7.41,11.8,null,null,null,null,null,null,11.4,1.4,7.4,11.5]
[0,0,10,10,"2017-10-21",3466.9368135682066,0.59,7.46,12,0.36699999999999999,7.41,11.9,null,null,null,null,null,null,14.5,1.21,7.4,11.2]
[0,0,10,10,"2017-10-22",3816.9056427056084,2.74,7.34,12.5,2.0499999999999998,7.31,12.1,null,null,null,null,null,null,15.2,1.1399999999999999,7.4,11.9]
[0,0,10,10,"2017-10-23",4233.2601216371686,0.49,7.47,13.9,0.13,7.46,13.4,null,null,null,null,null,null,12.9,1.33,7.4,13.4]
[0,0,10,10,"2017-10-24",3436.8418995542493,0.55000000000000004,7.47,13.5,0.3,7.46,13.4,null,null,null,null,null,null,13.6,1.34,7.4,13.2]
[0,0,10,10,"2017-10-25",3827.5643892925955,0.17,7.44,12.5,0.15,7.34,12.3,null,null,null,null,null,null,12.5,1.19,7.4,12.3]
[0,0,10,10,"2017-10-26",3920.806996646169,0.31,7.36,12.8,0.17,7.21,12.2,null,null,null,null,null,null,12.8,1.35,7.4,12]
[0,0,10,10,"2017-10-27",3293.7121745821737,0.4,7.41,12,0.21,7.34,12.1,null,null,null,null,null,null,13.8,1.26,7.4,11.1]
[0,0,10,10,"2017-10-28",3544.7758918631907,0.4,7.37,11.5,0.08,7.35,11.4,null,null,null,null,null,null,13.8,1.3,7.3,10.6]
[0,0,10,10,"2017-10-29",3574.5660201005153,0.33,7.48,11.8,0.24,7.46,11.4,null,null,null,null,null,null,14.5,1.2,7.4,11]
[0,0,10,10,"2017-10-30",3811.582818011404,0.42,7.44,11.5,0.14000000000000001,7.39,11.3,null,null,null,null,null,null,12,1.1100000000000001,7.4,11.2]
[0,0,10,10,"2017-10-31",4245.2773275394147,0.62,7.45,10.7,0.36,7.39,11.3,null,null,null,null,null,null,12.4,1.25,7.4,10.6]
[0,0,11,11,"2017-11-01",3335.773378752981,0.28000000000000003,7.45,10.9,0.15,7.4,10.9,null,null,null,null,null,null,12.1,1.22,7.4,10.4]
[0,0,11,11,"2017-11-02",3485.2498376363346,0.34,7.47,10.199999999999999,0.28000000000000003,7.42,10.1,null,null,null,null,null,null,13.5,1.35,7.4,9.8000000000000007]
[0,0,11,11,"2017-11-03",3854.3006599120245,0.48,7.54,9.6999999999999993,0.3,7.32,9.5,null,null,null,null,null,null,11.2,1.36,7.4,9.8000000000000007]
[0,0,11,11,"2017-11-04",4123.803694716421,0.42,7.52,10,0.33,7.41,9.1,null,null,null,null,null,null,12.2,1.3,7.5,9.4]
[0,0,11,11,"2017-11-05",3733.0089050414895,1.1299999999999999,7.49,9.8000000000000007,0.65,7.41,9.6,null,null,null,null,null,null,15,1.5,7.5,8.9]
[0,0,11,11,"2017-11-06",4191.390678376928,1.32,7.53,9.1999999999999993,0.71,7.61,8.4,null,null,null,null,null,null,13.8,1.4,7.6,8.1]
[0,0,11,11,"2017-11-07",4224.9798243237028,1.3,7.44,8.6999999999999993,0.93,7.37,8.6,null,null,null,null,null,null,14.6,1.37,7.4,7.9]
[0,0,11,11,"2017-11-08",3405.4834439078772,1,7.45,8,0.87,7.41,7.7,null,null,null,null,null,null,13,1.3,7.5,7.5]
[0,0,11,11,"2017-11-09",3346.4736144296921,0.7,7.47,8.3000000000000007,0.6,7.43,7.7,null,null,null,null,null,null,13.7,1.3,7.5,7]
[0,0,11,11,"2017-11-10",3326.8947406625957,0.98,7.39,7.4,0.8,7.41,7.3,null,null,null,null,null,null,14,1.4,7.5,7.1]
[0,0,11,11,"2017-11-11",3805.3606740747528,1.1000000000000001,7.37,7.9,1.05,7.29,7.8,null,null,null,null,null,null,11.6,1.28,7.5,6.6]
[0,0,11,11,"2017-11-12",3263.0239621027004,0.81,7.32,7,0.63,7.42,7,null,null,null,null,null,null,14.2,1.1599999999999999,7.5,6.6]
[0,0,11,11,"2017-11-13",4086.2286842629305,0.89,7.32,6.8,0.69,7.33,6.9,null,null,null,null,null,null,13.1,1.26,7.6,6.2]
[0,0,11,11,"2017-11-14",3940.7191081838332,0.88,7.34,6.6,0.84,7.35,6.5,null,null,null,null,null,null,13.2,1.24,7.4,6.2]
[0,0,11,11,"2017-11-15",3443.2500182151734,1.01,7.35,6.5,0.7,7.3,6.4,null,null,null,null,null,null,12.9,1.04,7.4,5.6]
[0,0,11,11,"2017-11-16",4031.135726122598,1.1599999999999999,7.29,6,0.78,7.34,6.4,null,null,null,null,null,null,12.2,1.18,7.4,6]
[0,0,11,11,"2017-11-17",3560.9713292679089,1.3,7.38,6.1,0.9,7.28,6.1,null,null,null,null,null,null,10.4,1.3,7.4,6.2]
[0,{"$f":"IF(MONTH(E329)=2,\"feb\",)","v":0},{"$f":"MONTH(E329)","v":11},11,"2017-11-18",3663.3193055066008,1,7.35,6.1,0.82,7.32,6.3,null,null,null,null,null,null,12.7,1.2,7.4,5.0999999999999996]
[0,0,11,11,"2017-11-19",3600.6532789728294,1.01,7.48,5.2,0.8,7.42,5.4,null,null,null,null,null,null,14.4,1.2,7.6,5.4]
[0,0,11,11,"2017-11-20",4318.528971556354,0.95,7.41,5.9,0.66,7.36,5.8,null,null,null,null,null,null,10.3,1.18,7.5,5.7]
[0,0,11,11,"2017-11-21",3784.8860418008035,0.66,7.46,5.8,0.59,7.34,5.8,null,null,null,null,null,null,11.4,1,7.5,5.4]
[0,0,11,11,"2017-11-22",4260.0318745750064,1.74,7.47,5.8,1.34,7.41,5.7,null,null,null,null,null,null,12.9,1.03,7.6,5.3]
[0,0,11,11,"2017-11-23",3420.8736663504346,1.02,7.39,5.4,0.82,7.37,4.8,null,null,null,null,null,null,11,1.2,7.6,4.5]
[0,0,11,11,"2017-11-24",4333.95926489266,1.1200000000000001,7.58,5.3,0.74,7.48,4.8,null,null,null,null,null,null,13,1.06,7.6,4.4000000000000004]
[0,0,11,11,"2017-11-25",3773.9573780802975,0.84,7.51,5.0999999999999996,0.48,7.45,5.2,null,null,null,null,null,null,13.2,1.2,7.5,4.8]
[0,0,11,11,"2017-11-26",3516.3646089073659,1,7.41,5.6,0.32,7.4,5.5,null,null,null,null,null,null,14.2,0.81,7.5,4.8]
[0,0,11,11,"2017-11-27",3580.428730935143,1,7.54,5.0999999999999996,0.53,7.53,5.3,null,null,null,null,null,null,14.7,1.22,7.6,4.8]
[0,0,11,11,"2017-11-28",3282.123793338923,1.01,7.56,5.3,0.88,7.53,5.7,null,null,null,null,null,null,14.2,1.2,7.6,4.7]
[0,0,11,11,"2017-11-29",3441.6053971419278,1,7.69,5.7,0.83,7.72,5.9,null,null,null,null,null,null,12.7,1.19,7.8,4.4000000000000004]
[0,0,11,11,"2017-11-30",3919.6337978349225,0.63,7.62,5.0999999999999996,0.6,7.54,5,null,null,null,null,null,null,13.8,1.2,7.6,5.0999999999999996]
[0,0,12,12,"2017-12-01",3426.7072872411595,0.87,7.59,6.2,0.61,7.55,6,null,null,null,null,null,null,13.9,1.06,7.7,5.4]
[0,0,12,12,"2017-12-02",3687.0666664737919,1.02,7.62,6,1.01,7.54,5.8,null,null,null,null,null,null,14.9,1.1100000000000001,7.7,5.4]
[0,0,12,12,"2017-12-03",3940.3066194354506,1.1000000000000001,7.71,5.0999999999999996,0.8,7.74,6,null,null,null,null,null,null,12.8,1.2,7.7,5.6]
[0,0,12,12,"2017-12-04",3292.7748958081156,1.7,8.4700000000000006,6.2,1.1000000000000001,8.15,6,null,null,null,null,null,null,13.4,1.2,8.1999999999999993,6.3]
[0,0,12,12,"2017-12-05",3369.7867444015465,0.9,7.59,5.7,0.69,7.39,5.9,null,null,null,null,null,null,13.5,1.06,7.7,5.7]
[0,0,12,12,"2017-12-06",4348.3392408583231,0.8,7.6,6.4,0.68,7.56,6,null,null,null,null,null,null,14.8,1,7.7,5.6]
[0,0,12,12,"2017-12-07",3529.3340664444736,1.01,7.64,6,0.82,7.61,5.8,null,null,null,null,null,null,14.1,0.92,7.6,5.5]
[0,0,12,12,"2017-12-08",3287.8799839107942,0.1,7.47,5.5,0.28999999999999998,7.57,5.6,null,null,null,null,null,null,15.3,1.17,7.6,4.2]
[0,0,12,12,"2017-12-09",3735.2299290715691,0.6,7.51,5.2,0.35,7.47,5.5,null,null,null,null,null,null,14.4,1.2,7.5,4.2]
[0,0,12,12,"2017-12-10",3981.7222733143976,0.3,7.69,5.4,0.24,7.62,5.0999999999999996,null,null,null,null,null,null,11.9,0.96,7.7,5]
[0,0,12,12,"2017-12-11",3967.4018505239801,0.42,7.47,5.8,0.36,7.54,5.6,null,null,null,null,null,null,8.5,0.78,7.7,5]
[0,0,12,12,"2017-12-12",3674.5624367730038,0.32,7.62,5.6,0.17,7.57,5.5,null,null,null,null,null,null,10.4,0.69,7.5,5.0999999999999996]
[0,0,12,12,"2017-12-13",4063.5701566046537,0.1,7.57,6,0.12,7.53,6.4,null,null,null,null,null,null,13.4,0.98,7.5,5.9]
[0,0,12,12,"2017-12-14",4320.9411103074572,0.62,7.61,5.4,0.28000000000000003,7.54,5.3,null,null,null,null,null,null,11.7,0.97,7.5,5.2]
[0,0,12,12,"2017-12-15",3883.6904822796309,0.43,7.77,5.4,0.13,7.47,6,null,null,null,null,null,null,12.6,0.87,7.6,5]
[0,0,12,12,"2017-12-16",3688.2821300286264,0.28000000000000003,7.5,6.9,0.16,7.51,5.4,null,null,null,null,null,null,14,0.94,7.6,5.5]
[0,0,12,12,"2017-12-17",3957.4280193772579,0.35,7.62,5.7,0.17,7.49,5.7,null,null,null,null,null,null,14.7,1,7.5,5.7]
[0,0,12,12,"2017-12-18",4095.7206119704365,0.33,7.65,6.5,0.17,7.62,6.7,null,null,null,null,null,null,13.8,0.93,7.6,6.1]
[0,0,12,12,"2017-12-19",4111.108414081611,0.5,7.64,5.4,0.2,7.63,6.5,null,null,null,null,null,null,12.3,0.94,7.6,5]
[0,0,12,12,"2017-12-20",4063.9378890083321,0.55000000000000004,7.54,5.5,0.34,7.57,5.4,null,null,null,null,null,null,14,0.91,8,5.0999999999999996]
[0,0,12,12,"2017-12-21",4277.8527928340209,0.3,7.66,5.9,0.16,7.53,5.9,null,null,null,null,null,null,14.2,0.9,7.6,6]
[0,0,12,12,"2017-12-22",4126.6019820870724,0.69,7.56,5.6,0.33,7.51,5.7,null,null,null,null,null,null,12.4,1,7.6,5]
[0,0,12,12,"2017-12-23",3647.0338516895736,0.34,7.49,5.8,0.3,7.46,5.7,null,null,null,null,null,null,12.6,1,7.6,5]
[0,0,12,12,"2017-12-24",4200.6073045854364,0.38,7.48,5.7,0.35,7.44,6.1,null,null,null,null,null,null,13.3,0.98,8,5.0999999999999996]
[0,0,12,12,"2017-12-25",3850.8194897162693,0.4,7.54,6.3,0.15,7.47,6.6,null,null,null,null,null,null,15.8,0.92,7.6,4.5]
[0,0,12,12,"2017-12-26",4080.3616655779674,0.43,7.65,6.1,0.22,7.55,6.4,null,null,null,null,null,null,14.3,0.94,7.6,4.5999999999999996]
[0,0,12,12,"2017-12-27",3663.5809298183503,0.49,7.64,5.7,0.2,7.5,6.2,null,null,null,null,null,null,13.1,0.93,7.6,4.7]
[0,0,12,12,"2017-12-28",4314.5664912142283,0.43,7.58,6.6,0.15,7.47,6.4,null,null,null,null,null,null,14,0.93,8,5.0999999999999996]
[0,0,12,12,"2017-12-29",3686.0728090181319,0.4,7.54,6,0.3,7.59,6.4,null,null,null,null,null,null,16.5,0.9,7.6,4.4000000000000004]
[0,0,12,12,"2017-12-30",4299.5454123177169,0.4,7.49,5.8,0.2,7.48,6.2,null,null,null,null,null,null,14.6,0.99,7.7,4.7]
[0,0,12,12,"2017-12-31",4193.7655586285928,0.32,7.62,6.2,0.11,7.5,6.3,null,null,null,null,null,null,13.5,0.85,7.5,5.9]
[0,0,{"$f":"IF(J3=1,MONTH(E373),13)","v":13},13,"2018-01-01"]

{"sheet":"MonthDist","index":17,"n_rows":42,"n_cols":40,"rows_kept":42,"cut":false,"hidden":true,"merged":[[5,2,5,4],[5,5,5,7],[5,8,5,10],[5,11,5,13]]}
["MONTH","RatioAvg","RatioMin","RatioMax","InactAvg","InactMin","InactMax"]
[{"$f":"MonthStart","v":"2017-12-01"},{"$f":"AVERAGE(MonthPlotOne)","v":4.1644682927765535},{"$f":"MIN(MonthPlotOne)","v":2.2660554940886648},{"$f":"MAX(MonthPlotOne)","v":5.922243158945637},{"$f":"AVERAGE(MonthPlotTwo)","v":4.1644682927765535},{"$f":"MIN(MonthPlotTwo)","v":2.2660554940886648},{"$f":"MAX(MonthPlotTwo)","v":5.922243158945637}]
[]
[]
["Monthly Data"]
[null,null,"Segment 1",null,null,"Segment 2",null,null,"Segment 3",null,null,"Segment 4",null,null,"Segment 5"]
["Date","Flow","Residual","pH","Temp.","Residual","pH","Temp.","Residual","pH","Temp.","Residual","pH","Temp.","Depth","Residual","pH","Temp.",null,null,"Seg1 CT-M","Seg1 CT-R","Seg1 Ratio","Seg2 CT-M","Seg2 CT-R","Seg2 Ratio","Seg3 CT-M","Seg3 CT-R","Seg3 Ratio","Seg4 CT M","Seg4 CT R","Seg4 Ratio","Seg5 CT M","Seg5 CT R","Seg5 Ratio","Total Ratio","Total Inact",null,"Total Ratio","Total Inact"]
[null,"gpm","mg/L",null,"C","mg/L",null,"C","mg/L",null,"C","mg/L",null,"C","ft","mg/L",null,"C",null,null,"mg/L-min","mg/L-min","M/R","mg/L-min","mg/L-min","M/R","mg/L-min","mg/L-min","M/R","mg/L-min","mg/L-min","M/R","mg/L-min","mg/L-min","M/R","M/R","Log",null,"M/R","Log"]
["2017-12-01",3426.7072872411595,0.87,7.59,6.2,0.61,7.55,6,null,null,null,null,null,null,13.9,1.06,7.7,5.4,null,null,{"$f":"IF(B9=\"\",,Seg1Vol*Seg1Fac/B9*C9)","v":0},{"$f":"Target*0.2828*D9^2.69*C9^0.15*0.933^(E9-5)","v":0},{"$f":"IF(V9=0,,U9/V9)","v":0},{"$f":"IF(B9=\"\",,Seg2Vol*Seg2Fac/B9*F9)","v":0},{"$f":"Target*0.2828*G9^2.69*F9^0.15*0.933^(H9-5)","v":0},{"$f":"IF(Y9=0,,X9/Y9)","v":0},{"$f":"IF(B9=\"\",,Seg3Vol*Seg3Fac/B9*I9)","v":0},{"$f":"Target*0.2828*J9^2.69*I9^0.15*0.933^(K9-5)","v":0},{"$f":"IF(AB9=0,,AA9/AB9)","v":0},{"$f":"IF(B9=\"\",,Seg4Vol*Seg4Fac/B9*L9)","v":0},{"$f":"Target*0.2828*M9^2.69*L9^0.15*0.933^(N9-5)","v":0},{"$f":"IF(AE9=0,,AD9/AE9)","v":0},{"$f":"IF(B9=\"\",,Seg5Vol*O9*Seg5Fac/B9*P9)","v":0},{"$f":"Target*0.2828*Q9^2.69*P9^0.15*0.933^(R9-5)","v":0},{"$f":"IF(AH9=0,,AG9/AH9)","v":0},{"$f":"W9+Z9+AC9+AF9+AI9","v":0},{"$f":"AJ9*Target","v":0},null,5.5004105894131294,5.5004105894131294]
["2017-12-02",3687.0666664737919,1.02,7.62,6,1.01,7.54,5.8,null,null,null,null,null,null,14.9,1.1100000000000001,7.7,5.4,null,null,{"$f":"IF(B10=\"\",,Seg1Vol*Seg1Fac/B10*C10)","v":0},{"$f":"Target*0.2828*D10^2.69*C10^0.15*0.933^(E10-5)","v":0},{"$f":"IF(V10=0,,U10/V10)","v":0},{"$f":"IF(B10=\"\",,Seg2Vol*Seg2Fac/B10*F10)","v":0},{"$f":"Target*0.2828*G10^2.69*F10^0.15*0.933^(H10-5)","v":0},{"$f":"IF(Y10=0,,X10/Y10)","v":0},{"$f":"IF(B10=\"\",,Seg3Vol*Seg3Fac/B10*I10)","v":0},{"$f":"Target*0.2828*J10^2.69*I10^0.15*0.933^(K10-5)","v":0},{"$f":"IF(AB10=0,,AA10/AB10)","v":0},{"$f":"IF(B10=\"\",,Seg4Vol*Seg4Fac/B10*L10)","v":0},{"$f":"Target*0.2828*M10^2.69*L10^0.15*0.933^(N10-5)","v":0},{"$f":"IF(AE10=0,,AD10/AE10)","v":0},{"$f":"IF(B10=\"\",,Seg5Vol*O10*Seg5Fac/B10*P10)","v":0},{"$f":"Target*0.2828*Q10^2.69*P10^0.15*0.933^(R10-5)","v":0},{"$f":"IF(AH10=0,,AG10/AH10)","v":0},0,{"$f":"AJ10*Target","v":0},null,5.7216051700699637,5.7216051700699637]
["2017-12-03",3940.3066194354506,1.1000000000000001,7.71,5.0999999999999996,0.8,7.74,6,null,null,null,null,null,null,12.8,1.2,7.7,5.6,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.0129227912966385,5.0129227912966385]
["2017-12-04",3292.7748958081156,1.7,8.4700000000000006,6.2,1.1000000000000001,8.15,6,null,null,null,null,null,null,13.4,1.2,8.1999999999999993,6.3,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.922243158945637,5.922243158945637]
["2017-12-05",3369.7867444015465,0.9,7.59,5.7,0.69,7.39,5.9,null,null,null,null,null,null,13.5,1.06,7.7,5.7,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.5591188611132178,5.5591188611132178]
["2017-12-06",4348.3392408583231,0.8,7.6,6.4,0.68,7.56,6,null,null,null,null,null,null,14.8,1,7.7,5.6,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,4.3839606522520596,4.3839606522520596]
["2017-12-07",3529.3340664444736,1.01,7.64,6,0.82,7.61,5.8,null,null,null,null,null,null,14.1,0.92,7.6,5.5,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.1924062289305626,5.1924062289305626]
["2017-12-08",3287.8799839107942,0.1,7.47,5.5,0.28999999999999998,7.57,5.6,null,null,null,null,null,null,15.3,1.17,7.6,4.2,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.4173172591850793,5.4173172591850793]
["2017-12-09",3735.2299290715691,0.6,7.51,5.2,0.35,7.47,5.5,null,null,null,null,null,null,14.4,1.2,7.5,4.2,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,5.2856742914943329,5.2856742914943329]
["2017-12-10",3981.7222733143976,0.3,7.69,5.4,0.24,7.62,5.0999999999999996,null,null,null,null,null,null,11.9,0.96,7.7,5,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,3.2450461215788891,3.2450461215788891]
["2017-12-11",3967.4018505239801,0.42,7.47,5.8,0.36,7.54,5.6,null,null,null,null,null,null,8.5,0.78,7.7,5,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,2.2660554940886648,2.2660554940886648]
["2017-12-12",3674.5624367730038,0.32,7.62,5.6,0.17,7.57,5.5,null,null,null,null,null,null,10.4,0.69,7.5,5.0999999999999996,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,2.6505616100072844,2.6505616100072844]
["2017-12-13",4063.5701566046537,0.1,7.57,6,0.12,7.53,6.4,null,null,null,null,null,null,13.4,0.98,7.5,5.9,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,3.8582777287744987,3.8582777287744987]
["2017-12-14",4320.9411103074572,0.62,7.61,5.4,0.28000000000000003,7.54,5.3,null,null,null,null,null,null,11.7,0.97,7.5,5.2,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,3.4872351831940378,3.4872351831940378]
["2017-12-15",3883.6904822796309,0.43,7.77,5.4,0.13,7.47,6,null,null,null,null,null,null,12.6,0.87,7.6,5,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,3.4569723820622773,3.4569723820622773]
["2017-12-16",3688.2821300286264,0.28000000000000003,7.5,6.9,0.16,7.51,5.4,null,null,null,null,null,null,14,0.94,7.6,5.5,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,4.2871985524161333,4.2871985524161333]
["2017-12-17",3957.4280193772579,0.35,7.62,5.7,0.17,7.49,5.7,null,null,null,null,null,null,14.7,1,7.5,5.7,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,4.6082905170441375,4.6082905170441375]
["2017-12-18",4095.7206119704365,0.33,7.65,6.5,0.17,7.62,6.7,null,null,null,null,null,null,13.8,0.93,7.6,6.1,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,3.9480940923982724,3.9480940923982724]
["2017-12-19",4111.108414081611,0.5,7.64,5.4,0.2,7.63,6.5,null,null,null,null,null,null,12.3,0.94,7.6,5,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,3.4728487132292241,3.4728487132292241]
["2017-12-20",4063.9378890083321,0.55000000000000004,7.54,5.5,0.34,7.57,5.4,null,null,null,null,null,null,14,0.91,8,5.0999999999999996,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,3.5046404256716306,3.5046404256716306]
["2017-12-21",4277.8527928340209,0.3,7.66,5.9,0.16,7.53,5.9,null,null,null,null,null,null,14.2,0.9,7.6,6,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,3.7136402536894919,3.7136402536894919]
["2017-12-22",4126.6019820870724,0.69,7.56,5.6,0.33,7.51,5.7,null,null,null,null,null,null,12.4,1,7.6,5,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,3.8423555138950136,3.8423555138950136]
["2017-12-23",3647.0338516895736,0.34,7.49,5.8,0.3,7.46,5.7,null,null,null,null,null,null,12.6,1,7.6,5,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,4.0608752269869468,4.0608752269869468]
["2017-12-24",4200.6073045854364,0.38,7.48,5.7,0.35,7.44,6.1,null,null,null,null,null,null,13.3,0.98,8,5.0999999999999996,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,3.2884002537076,3.2884002537076]
["2017-12-25",3850.8194897162693,0.4,7.54,6.3,0.15,7.47,6.6,null,null,null,null,null,null,15.8,0.92,7.6,4.5,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,4.3418633080525959,4.3418633080525959]
["2017-12-26",4080.3616655779674,0.43,7.65,6.1,0.22,7.55,6.4,null,null,null,null,null,null,14.3,0.94,7.6,4.5999999999999996,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,3.8472793537220049,3.8472793537220049]
["2017-12-27",3663.5809298183503,0.49,7.64,5.7,0.2,7.5,6.2,null,null,null,null,null,null,13.1,0.93,7.6,4.7,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,4.0108305996419196,4.0108305996419196]
["2017-12-28",4314.5664912142283,0.43,7.58,6.6,0.15,7.47,6.4,null,null,null,null,null,null,14,0.93,8,5.0999999999999996,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,3.264822678817398,3.264822678817398]
["2017-12-29",3686.0728090181319,0.4,7.54,6,0.3,7.59,6.4,null,null,null,null,null,null,16.5,0.9,7.6,4.4000000000000004,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,null,4.6083291878494972,4.6083291878494972]
["2017-12-30",4299.5454123177169,0.4,7.49,5.8,0.2,7.48,6.2,null,null,null,null,null,null,14.6,0.99,7.7,4.7,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,{"$f":"W38+Z38+AC38+AF38+AI38","v":0},0,null,3.757044158316587,3.757044158316587]
["2017-12-31",4193.7655586285928,0.32,7.62,6.2,0.11,7.5,6.3,null,null,null,null,null,null,13.5,0.85,7.5,5.9,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,{"$f":"W39+Z39+AC39+AF39+AI39","v":0},0,null,3.5821967182284391,3.5821967182284391]
[]
[]
[null,null,null,null,null,null,{"$f":"COUNT(Filter1)","v":31},{"$f":"COUNT(Filter2)","v":31},{"$f":"COUNT(Filter3)","v":0},{"$f":"COUNT(Filter4)","v":0},{"$f":"COUNT(Filter5)","v":0},{"$f":"COUNT(Filter6)","v":0}]